Feedback received following the Statutory Consultation carried out for the renewal of the IPPC application (IP 0001/09/A) for Poligas Ltd,  Hal Farrug Luqa

Timeframes: 24 April – 10 May 2017,     10 April - 24 April, 2018.

| Comment received from | Feedback dated May 2017 |  | ERA reply and comment |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Internal Consultees Feedback |  |  |  |  |  |  |  |
| Environmental Assessments | Kindly note that the Environmental Assessment Unit has no additional comments to make on this permit renewal. |  | No further actions required |  |  |  |  |
| Biodiversity and Water | Paragraph 2.2.6.6 of IP 0001/09 is noted: reference to the ‘LN 194 of 2004 as may be amended from time to time’ should be revised since this has been superseded by S.L. 549.100. |  | Noted |  |  |  |  |
| Ambient Quality & Waste - Air | No feedback provided. |  | - |  |  |  |  |
| Ambient Quality & Waste - Waste | No feedback provided. |  | - |  |  |  |  |
| Compliance & Enforcement Directorate | No feedback provided. |  | - |  |  |  |  |
| External Consultees Feedback |  |  |  |  |  |  |  |  |  |  |
| Comment received from | Feedback dated May 2017 | ERA reply and comment |  |  | Reply by applicant |  | Feedback dated April 2018 |  | Reply by applicant |  |
| REWS | The Regulator for Energy and Water Services has no comments to this Renewal. | - |  |  | - |  | No further comments |  |  |  |
| Water Services Corporation | From our end the only requirement we need is the enforcement of clause 2.2.3.1, the obtainment of a Public Sewer Discharge Permit as listed. We have made several inspections however we have not yet received an application from their end. Furthermore, is polimesh which is located beside Poligas considered within the scope of this IPPC permit? | Kindly note that in their original IPPC application the operator had indicated that there are no connections to the sewer from the permitted facility. In view that in your e-mail you have mentioned that WSC have carried out inspections on site – could you kindly confirm whether the statement in the original IPPC application is still valid. With regards to the Polimesh site, kindly note that this is not considered as falling within scope of the IPPC Permit. WSC Reply: I have checked with my colleagues and we are in agreement that Poligas do not have a direct physical connection to sewer, in that they have a cesspit. From the information we have collected this cesspit should only contain domestic effluent however this needs to be tested at least once to confirm this. Nonetheless we consider a cesspit to be indirectly connected given that this is ultimately discharged to our system. In my last email I have sent to poligas in October 2016, we have instructed them to install spill trays for some oil drums and also to forward some waste movement documents for empty paint cans. Even though they should have no trade effluent we still ask for some prevention measures. Thus in my opinion there shouldn’t be a differentiation between direct and indirect discharge as regards to sewage and hence this should be reflected in the IPPC permit. As regards polimesh, they use the same cesspit and given that the close proximity (i.e. one complex) and have the same ownership we consider them together. |  |  |  |  | We agree with the current clauses pertaining to the discharges into sewer however I have to point out the fact that PoliGas (and PoliMesh) have never applied for (nor obtained) a permit from us. We have visited the sites on different occasions however to no avail. Kindly remind them to contact us so they can regularise themselves through the permitting process. As regards firefighting issues, any such water used in the unfortunate event of a fire must not be drained to sewer. |  |  |  |
| OHSA | From the part of the OHSA, it is important that the applicant complies with all relevant Occupational Health and Safety regulations as stated in clause 2.7.3 in the permit. This site was not a COMAH site and as long as the inventory of dangerous substances has not increased, it should remain the same. |  |  |  |  | The employer is obliged to abide by all relevant health and safety regulations and in particular, in this case, with the Work Place (Minimum Health and Safety Requirements) Regulations L.N. 44 of 2002. These regulations specify that it is the duty of the employer to take all necessary measures with respect to fire safety at the workplace and ensure that the workplace is equipped at all times with suitable and sufficient fire-fighting equipment. These regulations also make reference to the Civil Protection Department which is the competent entity in fire safety. Hence OHSA is in agreement with the recommendations of the CPD. |  |  |  |  |
| MCCAA | No Feedback received |  |  |  |  |  |  |  |  |  |
| Planning Authority | No Feedback received |  |  |  |  |  |  |  |  |  |
| Environmental Health | No Feedback received |  |  | Refer to documents entitled “Application Documents” |  | Kindly note that this Directorate is in agreement with CPD recommendations. |  |  |  |  |
| Malta Resources Authority | Please note that the following paragraph needs to be updated, following the enactment of the REWS Act. 1. The Regulations for The Protection of Groundwater against Pollution caused by Certain Dangerous Substances have been revoked through Article 44 of said Act; and 2. The Water Policy Framework Regulations and the Protection of Groundwater against Pollution and Deteriorations Regulations do not fall any longer within the remit of the MRA by virtue of Articles 47 and 50 of said Act. |  |  |  |  | No Further comments |  |  |  |  |
| CPD | Reference is made to the meeting held at ERA on 13/06/2017. We all agree that gaseous fires are initially tackled by means of dry powder extinguishing media. This is usually the first method of control but if a number of cylinders are involved and there is a flame impingement on other cylinders or any other compressed gases and materials surrounding them, water will have to be used. Furthermore the use of water sprays to assist in the dispersal of gas and cooling of effected cylinders and other materials is also a requirement and hence the need to have a fire hydrant ring main. It should also be considered that any cylinder/s that has/have been involved in fire, exposed to heat or otherwise been dealt with as potentially hazardous must be left in position and, if possible, cooled by water spray for at least 24 hours. Therefore, if a period of 24 hours of cooling is required, this is another reason why the plant should be equipped with a fire hydrant system as no fire engine can supply water for 24 hours. The fire hydrant ring main should be made according to BS750 and should be capable of delivering not less than 2000 litres per minute at a non-static pressure of 3 bar. If the fire hydrants are placed underground, they should be clearly marked and should never be obstructed and the ring main should be made available 24/7. |  | Further to our meeting held at Hexagon House on 31st July 2017, kindly find below requests for information and clarifications from ERA and CPD. As discussed during the meeting, the provision of fire fighting water is primarily for cooling purposes and not to extinguish the fire. Thus the provision of a reliable water supply is deemed necessary in this regard. Further clarifications are kindly requested with respect to the below: 1. Kindly provide a site layout plan including location and capacity of all underground water reservoirs/cisterns which can be used for fire fighting purposes in case of a fire accident at the acetylene plant. In this regard, you are requested to indicate on the same plan access routes to the reservoirs and relevant dimensions to ensure that the fire brigade can easily access the area and be adequately manoeuvred so as to arrive near the water reservoir without them being subjected to undo damage or interference. 2. Kindly provide details about how the main reservoirs are connected to the 10m3 reservoir closest to the acetylene plant and details of any pumps (diesel+electric) that can be used to transfer additional water to the site area for fire fighting purposes. In this regard, you are kindly requested to provide details as to how the rates of the present pumps compares to the capacity of the water reservoirs to ensure that a reliable water supply can be maintained for cooling purposes. 3. A written declaration of the maximum amounts of acetylene cylinders and calcium carbide that can be stored at any one time on site and other secondary storage locations in the Polidano complex or off-site. 4. Kindly specify the amount of fire fighting material on site that can be used in case of calcium-carbide related accidents. Moreover, you are kindly requested to liaise with the CPD (in copy) in order to carry out a familiarisation visit to allow CPD to gain knowledge of the site, the whereabouts of the water reservoirs and availability of access. Please be reminded that should an emergency situation involving the cylinders take place, delays in cooling of this infrastructure and the surroundings could lead to domino effects on the neighbouring entities. |  |  | The CPD comments are the same, we have made it clear, we know that gas fires are extinguished with dry agent, but the applicant is only quoting what he wants to quote. in the same source that the applicant brought it was also state that cylinder involve should be cool wit conspicuous amount of water. This is the reason why we need water as there are cylinders involve we need to cool the cylinder with water. If an acetylene cylinder is subjected to a fire the whole cylinder needs to be cooled for 24 hours, because of its fragility. |  |  | Further to our conversation just now, attached please find pump specifications for CPD approval. Access for CPD will be adjacent to main gate as requested by CPD. Once we receive your approval works are expected to be completed within 1 month. | As Poligas are saying that they are going to install a pump to requirement we said, when the said pump is installed and is ready for us to inspect, they will inform us and we will inspect. It is important that the fire service put is not made near the entrance of the site but at least 18 metres away with a suitable fire service coupling that is quick release female instantaneous coupling. They should also see that the fire pump will start automatically, when the landing valve/s are opened. The last is that they also make sure that the reservoir is never left empty of water and is not used for anything except for this purpose. |