## Rating
Severity Scale - Including Magnitude/ reversibility / Long/short term effect |  |  |  | Occurence Scale |  |  |  | Detection Scale
| Effect | Criteria: Severity of Effect | Ranking | Probability of Failure | Time Period |  | Ranking | Detection | Criteria: Likelihood the existence of a deviation will be detected by process controls before next or subsequent process | Ranking
| Hazardous - Without Warning | May expose external stakeholder, operations and environment to major loss, harm or disruption - failure or harm will occur without warning | 10 | Very High: Failure is almost inevitable | More than once per day |  | 10 | Almost Impossible | No known controls available to detect failure mode - Out of boundary detection. | 10
| Hazardous - With Warning | May expose external stakeholder, operations and environment to loss, harm or disruption - failure or harm will occur with warning | 9 |  | Once every 3-4 days |  | 9 | Very Remote | Very remote likelihood current controls will detect failure mode - Out of boundary detection. | 9
| Very High | Major disruption of operation, resulting in either inconvenience or harm to any stakeholder and/or environment. | 8 | High: Generally associated with processes similar to previous processes that have often failed | Once every week |  | 8 | Remote | Remote likelihood current controls will detect failure mode - Out of boundary detection. | 8
| High | Minor disruption of operation, resulting in either inconvenience or harm to any stakeholder and/or environment. | 7 |  | Once every month |  | 7 | Very Low | Very low likelihood current controls will detect failure mode -Out of boundary detection. | 7
| Moderate | Major disruption of operations not involving external stakeholder and resulting in either inconvenience and/or harm to internal stakeholders and/or environment respectively. | 6 | Moderate: Generally associated with processes similar to previous processes which have experienced occasional failures, but not in major proportions | Once every 3 months |  | 6 | Low | Low likelihood current controls will detect failure mode - Within boundary | 6
| Low | Minor disruption of operations not involving external stakeholder and resulting in either inconvenience and/or harm to internal stakeholders and/or environment respectively. | 5 |  | Once every 6 months |  | 5 | Moderate | Moderate likelihood current controls will detect failure mode - Within boundary | 5
| Very Low | Minor disruption of operations involving internal stakeholder that may result in either minor inconvenience and/or harm to stakeholders and/or environment respectively. | 4 |  | Once a year |  | 4 | Moderately High | Moderately high likelihood current controls will detect failure mode - Within boundary | 4
| Minor | Minor disruption of service not involving any stakeholder and does not result in either inconvenience and/or harm to any stakeholders and/or environment respectively. | 3 | Low: Isolated failures associated with similar processes | Once every 1 - 3 years |  | 3 | High | High likelihood current controls will detect failure mode - At Source detection | 3
| Very Minor | No disruption of operations noticed by any stakeholders in any capacity and does not result in either inconvenience and/or harm to stakeholders and/or environment respectively. | 2 | Very Low: Only isolated failures associated with almost identical processes | Once every 3 - 6 years |  | 2 | Very High | Very high likelihood current controls will detect failure mode - At Source detection | 2
| None | No Effect | 1 | Remote: Failure is unlikely. No failures associated with almost identical processes | Once Every 7+ Years |  | 1 | Almost Certain | Current controls almost certain to detect the failure mode. Reliable detection controls are known with similar processes.- At Source detection | 1
| RPN Classification |  |  | Degree of Influence criteria | Value of the coefficient of influence | Criteria to evaluate the degree of influence
| High | 600 - 1000 |  | No influence | 0 | No opportunities to influence the impact
| Med | 300 - 600 |  | Low | 0.3 | Possibility to carry out information or awareness activities.
| Low | 1 - 300 |  | Medium | 0.5 | Possibility to address the impact through contracts, internal processes and supplier/contractors qualification and evaluation.
|  |  |  | High | 0.7 | The impact can be influenced through on site controls and supplier visits.
|  |  |  | Full | 1 | D3PG has direct influence on the aspect.

## FMEA
EMSR 05-01-EAIR_1 Environmental Aspects & Impacts Register | [55 empty] | ü - OFFSET
ü - ABNORMAL
ü - EMERGENCY
Review Date: May 2020 | [55 empty] | I- INTENDED OUTCOMES
PARTICIPANTS : ELMA PULIS, DAVID GRIXTI, IVAN CACHIA | [55 empty] | U-UNINTENDED OUTCOMES
COPY : Mr.Chen
PROCESS/AREA | [6 empty] | ENVIRONMENTAL IMPACTS | [19 empty] | QUALITY IMPACTS | [8 empty] | HS IMPACTS
[7 empty] | ADVERSE | OFFSET | INCREASE IN LANDFILL SPACE | DECREASE LANDFILL SPACE | DEPLETION OF NATURAL RESOURCES | CONSERVATION OF NATURAL RESOURCES | REDUCE, REUSE, RECYCLE | DEGRADATION OF ENVIRONMENT | ENVIRONMENTAL IMPROVEMENT | WATER TABLE & SOIL POLLUTION | SEA WATER POLLUTION | DEGRADATION OF WATER | AIR POLLUTION | GLOBAL WARMING | COMMUNITY & HEALTH ISSUES | SPILLS | EMS | Low impact BAT | Energy/Conservation | STAKEHOLDER DETRIMENT, HARM OR INJURY | STAKEHOLDER IMPACT | FINANCIAL IMPACT | PROCESS IMPACT | PDCA CYCLE | LEGAL IMPACT | PLANT MACHINERY | COMPETENCE & AWARENESS | DOCUMENTATION | Ref 2 | LEGAL IMPACT | WORK ENVIRONMENT | HEALTH IMPACT | SAFETY / HAZARDS IMPACT | SECURITY IMPACT | COMPETENCE & AWARENESS | x | NORMAL | ABNORMAL | EMERGENCY | POTENTIAL FAILURE MODE | POTENTIAL CAUSES OF FAILURE | CONTROL AND DETECTION | DEGREE OF INFLUENCE | SEVERITY | OCCURENCE | DETECTION | RPN 2019 - 2020 | OBJECTIVES & TARGETS | 2019 REVIEW and Risk Rating | Actions 2020 | Link to objectives 2020
To take into consideration: Law, Practical Control over Aspects, Cost, Time needed for completion, availability of reliable data, views of interested parties.
Ref 1 | Ref 2 | PROCESS/AREA | INPUTS / RESOURCES | OUTPUTS | ASPECTS | IMPACTS | [28 empty] | Ref 2
1 | 1 | PLANNING BUDGETING /RESOURCES | OFFICE EQUIPMENT FORECASTS TRENDS | REPORTS OFFICE WASTE PLANS EFFICIENCY IMPROVEMENT | 1. WASTE MANAGEMENT 2. INFLUENCE ON PROJECT | DECREASE IN LANDFILL SPACE DEGRADATION OF ENVIRONMENT WATER TABLE & SOIL POLLUTION ENVIRONMENTAL IMPROVEMENT CONSERVATION OF NATURAL RESOURES INCREASE LANDFILL SPACE REUSE, REDUCE, RECYCLE | ü | ü | ü | ü |  | ü | ü | ü | ü | ü | [10 empty] | ü | ü |  |  | ü | ü |  | ü | 1 | ü |  |  |  |  | ü |  | ü |  |  | PROJECT TARGETS NOT ACHIEVED | EXCEED BUDGETS INACCURATE PLANS PROJECT COMPLICATIONS CONTRACTOR ISSUES | #MONTHLY PLAN REVIEWS AND MITIGATION PLANS #CONTREACTOR CONTROLS ANDQHSE INSPECTION PLAN. #CONTRACTOR SELECTION CRITERIA | 1 | 7 | 6 | 6 | 252 | MANAGEMENT REVIEW MEETING IMPORVE CONTRACTOR SELECTION CRITERIA ENV/Q/HS | D3PG works mainly through contractors and by improving Supplier Selection Criteria, risk mitigation at planning stage should be made more effective. | OC 4 - Improvement of Supplier Selection Criteria to include QHSE aspects required. Improve the available Contractor Pack to a more comprehensive and stringent one. | OC 4
1 | 2 | PLANNING BUDGETING /RESOURCES | OFFICE EQUIPMENT FORECASTS TRENDS | REPORTS OFFICE WASTE PLANS EFFICIENCY IMPROVEMENT | 1. WASTE MANAGEMENT 2. INFLUENCE ON PROJECT | DECREASE IN LANDFILL SPACE DEGRADATION OF ENVIRONMENT WATER TABLE & SOIL POLLUTION ENVIRONMENTAL IMPROVEMENT CONSERVATION OF NATURAL RESOURES INCREASE LANDFILL SPACE REUSE, REDUCE, RECYCLE | ü | ü | ü | ü |  | ü | ü | ü | ü | ü | [10 empty] | ü | ü |  |  | ü | ü |  | ü | 2 | ü |  |  |  |  | ü |  | ü |  |  | FREQUENT STARTS AND STOPS | DISPATCH REQUIREMENTS BY ENE IN LINE WITH EXISITING PPA CONTRACTS OBLIGATIONS. | #ENGINES EXHAUST PATH TEMPERATURES - START AND STOPS OF ENGINES ARE PERFORMED ACCORDING TO DISPATCHE REQUIREMENTS, HOWEVER, WHEN FREQUENT START AN STOPS ARE REQUIRED ON D3PLANT THE PRACTICE IS TO START AND STOP AS MUCH AS PRACTICALLY POSSIBLE THE SAME ENGINES IN ORDER TO MAINTAIN ALMOST STEADY STATE TEMPERATURES ON EXHAUST PIPEWORK AND EQUIPMENT. SUCH OPERATIONAL STRATEGY WOULD ALLOW NOX ABATEMENT SYSTEMS ON RESPECTIVE ENGINES TO KICK IN JUST A FEW MINUTES AFTER ENGINE START. ON COLD ENGINES NOX ABATEMENT FUNCTION WOULD START AT A LATER STAGE ONCE EXHAUST STEADY STATE TEMPERATURES ARE REACHED. | 0.7 | 5 | 6 | 3 | 63
2I | 3 | PLANNING MAINTENANCE | OFFICE EQUIPMENT FORECASTS TRENDS | REPORTS OFFICE WASTE MAINTENANCE PLAN IMPROVED EQUIPMENT PERFORMANCE | 1. WASTE MANAGEMENT 2. PERFORMANCE EFFICIENCY | DECREASE IN LANDFILL SPACE DEGRADATION OF ENVIRONMENT WATER TABLE & SOIL POLLUTION GLOBAL WARMING ENVIRONMENTAL IMPROVEMENT CONSERVATION OF NATURAL RESOURES INCREASE LANDFILL SPACE REUSE, REDUCE, RECYCLE, REDUCED AIR POLLUTION | ü | ü | ü | ü |  | ü | ü | ü | ü | ü |  |  |  | ü | [6 empty] | ü | ü |  |  | ü | ü |  |  | 3 |  | ü | ü | ü |  |  |  | ü |  |  | PROJECTS AND PLAN SCHEDULES NOT MAINTAINED | NATURE O F DEMAND BY CUSTOMER AND AGREEMENTS IN PLACE OR UNPLANNED MAINTENANCE | #DAILY REVIEWS, WEEKLY MONITORING, MITIGATION AND #FLEXIBILITY TO ADAPT TO ARISING NEEDS. # ONSITE OEM REPS MONITORING MAIN PLANT MACHINERY #MAINTENANCE AND CALIBRATION PLANS | 0.5 | 5 | 3 | 3 | 22.5 |  | OC 1- Improve Maintenance System & develop a Calibration System to mo. nitor all measurement equipment at D3PG -.was fully implemented and risk rating improved.
2U | 4 | PLANNING MAINTENANCE |  | INACCURATE PLANS POSTPONED MAINTENANCE PARTS UNAVAILABILITY | PLANT MACHINERY ENERGY CONSUMPTION | AIR POLLUTION SEA POLLUTION LAND POLLUTION LEGAL IMPACT REDUCED PLANT OUTPUT STAKEHOLDER IMPACT LOW IMPACT BAT | ü | [8 empty] | ü | ü |  | ü |  |  |  |  | ü |  |  | ü |  |  |  | ü | ü |  |  | 4 |  | ü |  | ü |  |  |  |  | ü |  | POSTPONED /DELAYED MAINTENANCE PLANS & AVAILABILITY ISSUES. | # VARIYING OPERATIONAL DEMAND # MATERIAL ETA # OTHER MAJOR FAULTS | # DAILY OPERATIONAL HOURS MONITORING # ONSITE OEM REPS CONTROLLING RUNNING HR AND RELATED MAINTENANCE # CONTROL MECHANISMS IN THE PLANT | 0.7 | 5 | 6 | 3 | 63 | # TREND ANALYSIS # LIVE INFORMATION FLOW # AUTOMATIC SYSTEM UPDATES | OC 1- Improve Maintenance System & develop a Calibration System to mo nitor all measurement equipment at D3PG -.was fully implemented and risk rating improved. | Link review of contractor Calibration Systems to be audited e.g.: Inspections, Audits & procedures | OC 10
2U | 5 | PLANNING MAINTENANCE |  | UNPLANNED MAINTENANCE | PLANT MACHINERY ENERGY CONSUMPTION | AIR POLLUTION SEA POLLUTION LAND POLLUTION LEGAL IMPACT REDUCED PLANT OUTPUT STAKEHOLDER IMPACT LOW IMPACT BAT | ü | [8 empty] | ü | ü |  | ü |  |  |  |  | ü |  |  | ü |  |  |  | ü | ü |  |  | 5 |  | ü |  | ü |  |  |  |  | ü |  | ENGINES & EQUIPMENT MALFUNCTION | # VARIOUS | Preventive Plans are drawn according to OEM manuals for engines and all auxiliary equipemnt in addition : -Plant is manned on a 24 by 7 basis so as to monitor and attend at the earliest any malfunction. - Strategic spares are kept stored on site so as to avoid any waiting time to perform repairs -On planning plant dispatch we tend to keep one or two engines on stand by so that we can swap engines in service in case there is a malfunction on one of the running engines. | 0.7 | 5 | 6 | 3 | 63 | # TREND ANALYSIS # LIVE INFORMATION FLOW # AUTOMATIC SYSTEM UPDATES | OC 1- Improve Maintenance System & develop a Calibration System to mo nitor all measurement equipment at D3PG -.was fully implemented and risk rating improved. | Link review of contractor Calibration Systems to be audited e.g.: Inspections, Audits & procedures | OC 10
3I | 6 | ADMINISTRATION | OFFICE EQUIPMENT HUMAN RESOURCES HRM HS FINANCE TRAVEL | REPORTS TRAINING HS ACTIVITIES CSR ACTIVITIES PROVISION OF RESOURCES WASTE LEGAL COMPLIANCE | 1. WASTE MANAGEMENT 2. TRAINING & AWARENESS 3. MIXED WASTE 4. ENERGY/CONSERVATION | DECREASE IN LANDFILL SPACE DEGRADATION OF ENVIRONMENT WATER TABLE & SOIL POLLUTION GLOBAL WARMING ENVIRONMENTAL IMPROVEMENT CONSERVATION OF NATURAL RESOURES INCREASE LANDFILL SPACE REUSE, REDUCE, RECYCLE H&S AWARENESS | ü | ü | ü | ü |  | ü | ü | ü | ü | ü |  |  |  | ü |  |  |  |  | ü |  | ü |  |  | ü | ü | ü |  | ü | 6 | ü | ü |  |  |  | ü | ü | ü |  |  | NEW LEGISLATION AND DELAYED COMPLIANCE | BUREAUCRACY & CONFLICTING LEGISLATION WITH MOTHER COMPANY | LEGAL COMPLAINCE EXERCISE ON A YEARLY BASIS | 1 | 8 | 7 | 5 | 280 | GDPR IMPLEMENTATION ENERGY AUDIT ENERGY POLICY |  | OC 1 - Energy Management & OC 9 - Standardised Processes | OC 1 OC 9
3U | 7 | ADMINISTRATION |  | LACK OF RESOURCES LACK OF TRAINING LEGAL COMPLAINCE | 1. MIXED WASTE 3. LEGAL BREACHES | DECREASE IN LANDFILL SPACE DEGRADATION OF ENVIRONMENT WATER TABLE & SOIL POLLUTION GLOBAL WARMING ENVIRONMENTAL DETRIMENT STAKEHOLDER DETRIMENT, HARM OR INJURY | ü |  |  | ü |  |  |  | ü | ü | ü |  |  | ü | ü | ü |  | ü |  |  | ü | ü |  |  |  | ü |  |  |  | 7 | ü | ü |  |  |  | ü | ü | ü | ü |  | FAILURE TO IDENTIFY NEW LEGISATIONS IN TERMS OF ALL ADMINISTRATION | LACK OF INFORMATION, TRAINING AND RESOURCES | # SYSTEMS TO DETECT NEW LEGISLATION - IPPC, HS OFFICER, LEGAL COMPLIANCE EXERCISE. # TRAINING AND DEVELOPMENT MANAGEMENT IN PLACE #CONTRACTOR COMMUNICATION & CONTROL. | 1 | 6 | 5 | 7 | 210 | #ENFORCE RESOURCE PLANNING AND INTERNAL / EXTERNAL #COMMUNICATION CHANNELS.-CONTRACTORS # MAINTAIN LEGAL COMPLIANCE REVIEW YEARLY. |  | To establish Share point with IESC & To upload D3PG Policies on the website | IESC Shared Server for all the relevant documents and records. OC 6 /2019
4I | 8 | PROCUREMENT | PURCHASE REQUISITIONS PROCEDURES SPECS & DOCS MSDS | PO PARTS AVAIALBILITY SUPPLIER RELATIONS SUPPPLIER INFULENCE PRINTED RECORDS & DATA MSDS | 1. INFLUENCE 2. RESOURCES | ENVIRONMENTAL IMPROVEMENT DEPELETION OF NATURAL RESOURCES | ü | ü |  |  | ü |  |  |  | ü | [11 empty] | ü |  |  |  |  | ü |  | ü | 8 | [7 empty] | ü |  |  | STOCK CONTROL WRONG PARTS | POOR STOCK MANAGEMENT | 3 | 1 | 5 | 5 | 4 | 100 | IMPLEMENTATION OF ACCUMATICA SYSTEM TO IMPROVE: 1. OPERATIONAL EFFICIENCY 2. CONTRACTOR CONTROL. 3. NO PAPER RECORDS. 4. STOCK LEVEL CONTROL | NEW ERP IMPLEMENTATION TO IMPORVE STOCK CONTROL AND PROCESS EFFICIENCY. | PFMEA reviewed following ERP Oracle upgrade | OC 4
4U | 9 | PROCUREMENT |  | # LONG ETA # LONGER TRANSPORTATION ROUTES | 1. INFLUENCE 2. RESOURCES 3. TRANSPORTATION 4.STAKEHOLDER IMPACT 5. LEGAL IMPACT PLANT MACHINERY | ENVIRONMENTAL IMPROVEMENT AIR POLLUTION SEA POLLUTION LAND POLLUTION DEPLETION OF NATURAL RESOURCES | ü |  |  |  | ü |  |  |  | ü | ü | ü |  | ü | [7 empty] | ü | ü | ü |  |  | ü |  | ü | 9 | ü |  |  | ü |  |  |  |  | ü |  | #PARTS UNAVAILBILITY #INTRODUCTION OF NEW CHEMICALS #CONTRACT BREACH | OEM PARTS ETA ISLAND LOGISTIC UNFORSEEN EVENTS POOR STOCK MANAGEMENT #NO SDS AVAIALBILITY & NO DISTRIBUTION THEREOF | DETECTED AND CONTROLLED THROUGH COMMUNICATION AND RELATIONSHIP BUILDING WITH THE SUPPLIERS #SDS CONTROL SYSTEM INTRODUCED THROUGH PROCUREMENT #SUPPLIER SELECTION & CRITERIA IMPROVEMENT WHERE APPLICABLE | 0.7 | 8 | 5 | 7 | 196 | IMPROVE SUPPLIER SELECTION CRITERIA TO INCLUDE QUALITY, ENVIRONMENTAL AND HS ASPECTS | Supplier Evolution carried out manually for 2019. To follow every year accordingly. Actions taken following Supplier evaluation 2019 | Automate Supplier evaluation in new ERP Include automated KPI in new ERP | OC 4
5 | 10 | LOGISTICS | PO SPECS & DOCS PACKAGING NOTES | RELEASED PARTS PRINTED RECORDS AND DOCUMENTS | 1. INFLUENCE 2. WASTE MANAGEMENT 3. TRANSPORTATION 4. RESOURCES | ENVIRONMENTAL IMPROVEMENT CONSERVATION OF NATURAL RESOURES INCREASE LANDFILL SPACE REUSE, REDUCE, RECYCLE AIR POLLUTION SEA POLLUTION GLOBAL WARMING DEPLETION OF NATURAL RESOURCES | ü | ü | ü |  | ü | ü | ü |  | ü | ü | ü |  | ü | ü | [6 empty] | ü | ü |  |  | ü | ü |  | ü | 10 |  |  |  | ü |  |  |  | ü |  |  | #INCREASED /NEW PACKAGING # CHEMICAL TRANSPORTATION & HANDLING ISSUES | # SUPPLIER CHANGES IN PACKAGING #NEW SUPPLIER #LACK OF DOCUMENTATION & LEGAL REQUIREMENTS | MAINTAIN AN OPEN DIALOGUE AND CONTRACTUAL OBLIGATIONS TO ENSURE CHANGES ON MATERIAL AND PACKAGING ARE COMMUNICATED BY THE SUPPLIER. | 0.3 | 7 | 8 | 7 | 117.6 | IMPLEMENT GREEN LOGISTICS, INCLUDING SUGGESTIONS FOR PACKAGING IMPROVEMENT AND POSSIBLE ECO FRIENDLY MATERIAL |  | POSSIBLE INCLUSION OF ENVIRONMENTAL INFLUENCE | OC 4
6 | 11 | WAREHOUSING | SPARE PARTS PROCEDURES PPE EQUIPMENT MATERIAL SPECS/DOCUMENTS CHEMICALS TRAINED EMPLOYEES | RECORDS COA RELEASED SPARE PARTS GREEN LOGISTICS REDUCTION IN PACKAGING PACKAGING WASTE | 1. MIXED WASTE 2. WASTE MANAGEMENT 3. INFLUENCE | DECREASE IN LANDFILL SPACE DEGRADATION OF ENVIRONMENT WATER TABLE & SOIL POLLUTION GLOBAL WARMING ENVIRONMENTAL IMPROVEMENT CONSERVATION OF NATURAL RESOURES INCREASE LANDFILL SPACE REUSE, REDUCE, RECYCLE ENVIRONMENTAL IMPROVEMENT | ü | ü | ü | ü |  | ü | ü | ü | ü | ü |  |  |  | ü | [11 empty] | ü |  | ü | 11 | [7 empty] | ü |  |  | LACK OF SPACE FOR STORAGE DAMAGED PARTS. PARTS FROM ENE WAREHOUSE ARE DELIVERED DAMAGED # WAREHOUSING LIMITATIONS | OCCASIONAL LARGER MATERIAL REQUIREMENT FOR MAJOR OVERHAULS. INAPPROPRIATE HANDLING (BY NOT REPORTING OR DAMAGING) AT EMC STORES #WAREHOUISING CONTRACTS AND RELATED ISSUES | MAINTAIN LOW STOCKS ENSURE MATERIAL PURCAHSED IS PLANNED FOR OPERATION. SUPPLIER ACCOUNTABILITY | 0.7 | 7 | 7 | 5 | 171.5 | AGREEMENTS WITH SUPPLIERS TO KEEP STOCKS AT THEIR LOCATION. POSSIBLE SUPPORT FROM EMC IN THEIR WAREHOUSE. SUPPLIER COMPLAINT SYSTEM & SUPPLIER EVALUATION PROCESS. |  | Warehousing Feasibility study in view of contract expiration. | OC 4
6U | 12 | WAREHOUSING | UNTRAINED EMPLOYEES | DAMAGED PARTS NC MATERIAL CHEMICAL SPILLS | 1. TRANSPORTATION 2. INFLUENCE 3. ENERGY CONSUMPTION 4. SPILLS 5. BAD WAREHOUSING PRACTICES | AIR POLLUTION SEA POLLUTION GLOBAL WARMING DEPLETION OF NATURAL RESOURCES ENVIRONMENTAL IMPROVEMENT DEGRADATION OF ENVIRONMENT DECREASE IN LANDFILL SPACE WATER TABLE & SOIL POLLUTION | ü | ü | ü | ü |  | ü | ü | ü | ü | ü |  |  |  | ü |  |  |  |  | ü |  | ü | ü | ü |  |  | ü | ü |  | 12 | ü | ü |  | ü |  | ü |  | ü | ü |  | #DAMAGED / UNAVAILABLE PARTS # BAD WAREHOUSING PRACTICES | TRANSPORTATION DAMAGE WRONG PARTS DELIVERED WRONG PARTS ORDERED INJURY OR HARM TO EMPLOYEES | # IMPROVE REQUISITION CONTROL SYSTEM WITH IESC # BUNDING FOR CHEMICALS # SUPPLIER COMMUNICATION #AUDIT CONTRACTOR TRAINING & COMPETENCE. | 0.7 | 4 | 6 | 4 | 67.2 | # IMPLEMENT SUPPLIER COMPLAINT SYSTEM AND DEVELOP SUPPLIER RELATIONSHIP # IESC PROCEDURE AND CONTROLS TO ENSURE CORRECT PARTS ORDERING AS PER BLUE FILES.
7 | 13 | EXHAUST PATH & ABATEMENT | UREA ABATEMENT SCR CATALYSTS CEMS | WASTE STACK EMISSIONS NOISE EMISSIONS | 1. EMISSIONS TO AIR - NOx , CO 2. WASTE MANAGEMENT (CATALYTIC REACTOR FILTERS) 3. BAT | ENVIRONMENTAL IMPROVEMENT CONSERVATION OF NATURAL RESOURES INCREASE LANDFILL SPACE REUSE, REDUCE, RECYCLE GLOBAL WARMING AIR POLLUTION LOW IMPACT BAT | ü | ü | ü | ü |  | ü | ü |  | ü |  |  |  |  | ü |  |  |  | ü | [6 empty] | ü |  |  | ü | 13 | [7 empty] | ü |  |  | VARIATION OF NOX & CO EMISSIONS OUT OF GIVEN LIMITS #LEGAL REPORTING ISSUES | #POSSIBLE UREA INJECTION FAILURES #SPENT CATALYST | # DOSING CONTROLLER # CEMS EMISSIONS CONTROL # CALIBRATION # AST # OXIDISATION CATALYST | 1 | 6 | 2 | 5 | 60 | CEMS WILL BE IMPROVED FOR BETTER MONITORING SYSYTEM AND REPORTING. | CEMS upgrade was implemented. Currently being tested. ASTs in 2019 confirmed that the Dust Sensors are in good working condition, replacement is not planned as yet.
7U1 | 14 | EXHAUST PATH & ABATEMENT |  | EXHAUST LEAKS SCR CATALYSTS | 1. EMISSIONS TO AIR - NOx ,CO 2. WASTE MANAGEMENT | GLOBAL WARMING AIR POLLUTION ENVIRONMENTAL IMPROVEMENT CONSERVATION OF NATURAL RESOURES INCREASE LANDFILL SPACE REUSE, REDUCE, RECYCLE LOW IMPACT BAT | ü | ü | ü |  |  | ü | ü |  | ü |  |  |  | ü | ü |  |  |  | ü | [10 empty] | 14 | [7 empty] | ü | ü |  | EMISSIONS TO AIR | DAMAGED PIPE WORKS | REGULAR NSPECTIONS AND CONTROLS | 1 | 4 | 2 | 3 | 24 | BAT NOT MUCH IMPROVEMENT TO BE IMPLEMENTED ATM
7U2 | 15 | EXHAUST PATH & ABATEMENT |  | EXHAUST CONDENSATION | 3. WASTE MANAGEMENT - OILY WATER | ENVIRONMENTAL IMPROVEMENT CONSERVATION OF NATURAL RESOURES INCREASE LANDFILL SPACE REUSE, REDUCE, RECYCLE LOW IMPACT BAT | ü | ü | ü |  |  | ü | ü |  | ü | [8 empty] | ü | [10 empty] | 15 | [7 empty] | ü | ü |  | OILY WATER ST OUTFALL | DIRTY INTERCEPTORS | VISUAL AND ODOROUS REGULAR INSPECTIONS | 1 | 5 | 2 | 4 | 40 |  | Interceptor Checks were improved as per EMSP 03-03-II_2
7U3 | 16 | EXHAUST PATH & ABATEMENT |  | INCORRECT CEMS READINGS | 1. EMISSIONS TO AIR - NOx ,CO | ENVIRONMENTAL IMPROVEMENT CONSERVATION OF NATURAL RESOURES INCREASE LANDFILL SPACE REUSE, REDUCE, RECYCLE LOW IMPACT BAT | ü | [16 empty] | ü | [10 empty] | 16 | [7 empty] | ü | ü |  | CEMS MALFUNCTION | VARIOUS | #REGULAR CALIBRATION #CONTINUOUS MONITORING #CONTRACT WITH SUNLAB FOR IMMEDIATE SUPPORT LOCALLY OR ABROAD IN CASE OF MALFUNCTIONS | 1 | 5 | 2 | 4 | 40
7U4 | 17 | EXHAUST PATH & ABATEMENT |  | TRAPPED GASES IN PATH | 4. EMISSIONS TO AIR - UNBURNT GAS | GLOBAL WARMING AIR POLLUTION | ü | [11 empty] | ü | ü | [6 empty] | ü | ü |  |  |  | ü |  |  | 17 |  | ü |  | ü | [5 empty] | ü | ENGINE NOT STARTING | TRAPPED GASES | # PURGE FANS # RUPTURE DISKS DIRECTED AND PROTECTED BY GUARDS | 1 | 7 | 4 | 6 | 168 | MAINTAIN A SAFE ENVIRONMENT | Engine 43 accident in 2018 was linked to this. All recommendations were implemented as per Wartsila report. | A study was commissioned to Wartsila to simulate the exhaust pipe system and suggest improvement to the physical set up in case of over pressure. | OC 10
8 | 18 | AUXILIARY BOILER | DIESEL | VENT VALVES PRESSURE RELEASE VALVES INERT GAS PURGING STACK EMISSIONS | 1. EMISSIONS TO AIR | GLOBAL WARMING AIR POLLUTION | ü | [11 empty] | ü | ü | [14 empty] | 18 | [7 empty] | ü |  |  | INCREASED EMISSIONS | EQUIPMENT MALFUNCTION | CERTIFICATION OF EMISSIONS EVERY 3 YEARS VISUAL DETECTION OF STEAM REGULAR MAINTENANANCE AS PER OEM | 1 | 4 | 4 | 4 | 64 | ENSURE EMISSIONS CONTROL |  | AUXILIARY BOILER TESTS AVAILABLE FOR 2020 | OC 10
9I1 | 19 | FUEL SYSTEM & LINES | DIESEL NATURAL GAS DIESEL TANK | PILOT FUEL FILTERS | 1. EMISSIONS TO AIR 2. WASTE MANAGEMENT 3. BAT 4. RESOURCES | ENVIRONMENTAL IMPROVEMENT CONSERVATION OF NATURAL RESOURES INCREASE LANDFILL SPACE REUSE, REDUCE, RECYCLE GLOBAL WARMING AIR POLLUTION DEPLETION OF NATURAL RESOURCES | ü |  | ü | ü | ü | ü | ü |  | ü |  |  |  |  | ü | [14 empty] | 19 | [7 empty] | ü |  |  | DROP IN PRESSURE | CLOGGED FILTER | DCS PILOT FUEL PRESSURE WILL BE HIGHLIGHTED AND SWITCHED ON MANUALLY. | 1 | 4 | 4 | 2 | 32 |  | DCS was upgraded in 2019.
9I2 | 20 | FUEL SYSTEM & LINES | DIESEL NATURAL GAS DIESEL TANK | VENTING TO ATMOSPHERE | 6. EMISSIONS TO AIR | GLOBAL WARMING AIR POLLUTION | ü |  | ü | ü | ü | ü | ü |  | ü |  |  |  |  | ü | [14 empty] | 20 | [7 empty] | ü |  |  | STUCK OPEN VALVES | WEAR AND TEAR | SYSTEM DETECTION IS IMMEDIATE | 1 | 2 | 8 | 2 | 32 |  | DCS was upgraded in 2019.
9U1 | 21 | FUEL SYSTEM & LINES |  | FUEL LEAKS DUE TO FLANGE ISSUES PILOT SPILLAGE (Diesel) LEAKS ON RACKS | 3. EMISSIONS TO SEA 4. EMISSIONS TO LAND | SEA POLLUTION ENDANGERING ECOSYSTEM COMMUNITY & HEALTH ISSUES WATER TABLE & SOIL POLLUTION | ü | [8 empty] | ü | ü | ü |  |  | ü | [10 empty] | ü |  |  | 21 | [8 empty] | ü |  | LEAKS AND SPILLS | DAMAGED PUMPS OR PIPEWORK | # SPILL TRAY CONNECTED TO ENGINE 45 SLUDGE TANK. # RECORDED GAS LINE AND FLANGE INSPECTIONS. # ENGINE SENSOR AND SHUTDOWN DUE TO LOW PRESSURE. # SPILLAGE RESPONSE PLAN # ATEX ZONES - EQUIPMENT IN ZONES COMPATIBILITY | 0.8 | 4 | 4 | 5 | 64
9U2 | 22 | FUEL SYSTEM & LINES | GAS FUEL FILTERS | FILTERS | 5. WASTE MANAGEMENT | ENVIRONMENTAL IMPROVEMENT CONSERVATION OF NATURAL RESOURES INCREASE LANDFILL SPACE REUSE, REDUCE, RECYCLE | ü |  | ü |  |  | ü | ü |  | ü | [16 empty] | ü |  |  | 22 | [8 empty] | ü |  | FILTER WEAR AND TEAR AND/OR DAMAGE | EXTERNAL CONTAMINANT | FILTER REPLACEMENT IN ACCORDANCE TO MAINTENANCE PLAN. (@4000HRS) | 1 | 2 | 2 | 2 | 8 |  | DCS was upgraded in 2019.
9U3 | 23 | FUEL SYSTEM & LINES |  | GAS LEAKS | 6. EMISSIONS TO AIR | GLOBAL WARMING AIR POLLUTION | ü | [11 empty] | ü | ü | [14 empty] | 23 |  |  |  | ü |  |  |  |  | ü |  | PIPEWORK DAMAGE | CORROSION AND TAP OFFS | # VENTING TO ATMOSPHERE THROUGH A PRESSURED SYSTEM FOLLOWING ENGINE SHUT DOWN. # WEEKLY LEAK TEST ON FLANGES # MONTHLY GAS LEAK CHECKS # CONTINUOUS GAS AND METHANE DETECTION IN ENGINE ENCLOSURE. | 0.7 | 4 | 5 | 4 | 56 |  | Independent engineer certification during Dec 2019
10 | 24 | LUBRICATION OILS | RESERVOIR FLANGES AND PIPING | OIL REPLACEMENT | 1. WASTE MANAGEMENT 2. RESOURCES | ENVIRONMENTAL IMPROVEMENT CONSERVATION OF NATURAL RESOURES INCREASE LANDFILL SPACE REUSE, REDUCE, RECYCLE DEPLETION OF NATURAL RESOURCES | ü |  | ü |  | ü | ü | ü |  | ü | [16 empty] | ü |  |  | 24 | [7 empty] | ü |  |  | OIL SPILLS | HUMAN ERROR | # OPERATIONAL PROCEDURES & CONTAINNMENT MEASURES INPLACE # SPILL KITS # TRAINED EMPLOYEES | 1 | 6 | 1 | 1 | 6
10U1 | 25 | LUBRICATION OILS | RESERVOIR FLANGES AND PIPING | FLANGE LEAKS LEAKS IN ENGINE ROOMS SPILLS | 3. EMISSIONS TO LAND 4. EMISSIONS TO SEA 5. SPILLS | SEA POLLUTION ENDANGERING ECOSYSTEM COMMUNITY & HEALTH ISSUES WATER TABLE & SOIL POLLUTION DEGRADATION OF ENVIRONMENT DECREASE IN LANDFILL SPACE | ü |  |  | ü |  |  |  | ü |  | ü |  | ü |  |  | ü | [6 empty] | ü | [6 empty] | 25 | [8 empty] | ü |  | OIL LEAKS | # LACK OF TRAINING # DAMAGED IBCS # DAMAGED FLANGES | # BUNDED AREAS # SPILL KITS # FLANGE CHECKS # ENGINE ROOM PITS WITH CONNECTION TO OILY WATER #INTERCEPTORS AND SLUDGE TANKS | 0.7 | 6 | 4 | 2 | 33.6
11 | 26 | DAY TANKS - DIESEL AND OIL | TANKS FUEL | FUEL SUPPLY | 1. RESOURCES | DEPLETION OF NATURAL RESOURCES | ü |  |  |  | ü | [5 empty] | ü |  | ü | ü | [14 empty] | 26 | [7 empty] | ü | [5 empty] | 0.5 | 5 | 7 | 1 | 17.5
11U1 | 27 | DAY TANKS - DIESEL AND OIL | TANKS FUEL | LEAKS SPILLS OVERFLOW | 3. EMISSIONS TO LAND 4. EMISSIONS TO SEA 5. SPILLS | SEA POLLUTION ENDANGERING ECOSYSTEM COMMUNITY & HEALTH ISSUES WATER TABLE & SOIL POLLUTION DEGRADATION OF ENVIRONMENT DECREASE IN LANDFILL SPACE | ü |  |  | ü |  |  |  | ü |  | ü |  | ü |  |  | ü | [6 empty] | ü | [6 empty] | 27 | [8 empty] | ü |  | SPILLAGES LEAKS | # HUMAN ERROR # FAULTY SENSORS # DAMAGED TANKS | # HIGH LEVEL SENSORS # BUNDED AREA # BUNDED AREA CERTIFICATIONS # OVERFLOW TO OILY WATER TANKS # TANKS CERTIFICATION | 1 | 4 | 2 | 3 | 24
12 | 28 | SEA WATER COOLING PATH SYSTEM | PIPING CHEMICALS FOR ANTI SCALING AND ANTI CHLORINATION | HIGH TEMPERATURE AT DISCHARGE CHEMICALS AT OUTFALL ANODES IN CLUDED TO ELIMINATE GALVANIC CURRENTS TO AVOID CORROSION | 1. EMISSIONS TO SEA | SEA POLLUTION ENDANGERING ECOSYSTEM COMMUNITY & HEALTH ISSUES | ü | [9 empty] | ü | ü |  |  | ü | [13 empty] | 28 | [7 empty] | ü |  |  | LEAKS IN ROCK | CRACKED PIPING BURIED IN ROCKS |  | 1 | 1 | 1 | 1 | 1
12U1 | 29 | SEA WATER COOLING PATH SYSTEM | PIPING CHEMICALS FOR ANTI SCALING AND ANTI CHLORINATION | EXCESSIVE CHEMICAL DOSING | 2. EMISSIONS TO SEA 3. CHEMICALS | SEA POLLUTION ENDANGERING ECOSYSTEM COMMUNITY & HEALTH ISSUES | ü | [9 empty] | ü | ü |  |  | ü |  |  |  | ü | [6 empty] | ü |  |  | 29 | [7 empty] | ü | ü |  | CHEMICALS EXCEEDING ACCEPTANCE RANGE | SENSOR FAULTS LACK OF ADEQUATE MAINTENANCE | # COOLING SYSTEM TO MAINTAIN A MAX 8C TEMP AT THE DISCHARGE POINT. # CONTROLLED AND REGULATED CHEMICAL THROUGH IPPC AND SAMPLING # CONTINUOUS TEMPERATURE AND PH MONITORING. # 6 MONTHLY INSPECTION ANODE CONDENSOR AND DOWN CONDENSOR | 1 | 8 | 3 | 7 | 168 | MAINTAIN AN EFFECTIVE COOLING SYSTEM | One seawater pump was overhauled in 2019. The other one, Sea water pump 1. will be overhauled in 2020 | To overhaul the cooling water pump | OC 10
13 | 30 | OILY WATER AND SLUDGE COLLECTION SYSTEM | BURNT OIL FUEL LINES COALESCER | OIL SLUDGE FILTERED WATER | 1. EMISSIONS TO LAND 2. EMISSIONS TO SEA 3. EMISSIONS TO AIR 4. WASTE MANAGEMENT | GLOBAL WARMING AIR POLLUTION WATER TABLE & SOIL POLLUTION SEA POLLUTION ENDANGERING ECOSYSTEM COMMUNITY & HEALTH ISSUES ENVIRONMENTAL IMPROVEMENT CONSERVATION OF NATURAL RESOURES INCREASE LANDFILL SPACE REUSE, REDUCE, RECYCLE | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü | ü | ü | ü | [13 empty] | 30 | [7 empty] | ü |  |  | OIL SLUDGE DISPERSION DURING MOVEMENT | HUMAN ERROR | BUNDS & SPILL KITS | 1 | 3 | 2 | 2 | 12
13U1 | 31 | OILY WATER AND SLUDGE COLLECTION SYSTEM | BURNT OIL FUEL LINES | LEAKING /CRACKED INTERCEPTORS SPILLS | 5. EMISSIONS TO SEA 6. EMISSIONS LAND | WATER TABLE & SOIL POLLUTION SEA POLLUTION ENDANGERING ECOSYSTEM COMMUNITY & HEALTH ISSUES | ü | [8 empty] | ü | ü | ü |  |  | ü |  |  |  | ü | [9 empty] | 31 | [7 empty] | ü | ü |  | VISIBLE OIL AT OUTFALL | CRACKED INTERCEPTORS FLANGE LEAKS | # OIL AND HYDROCARBON SENSORS AT ENEMALTA INTERCEPTORS. # PPM MEASUREMENT AT FRONTAL OUTFALL. # ROUTINE INSPECTION AS PER IPPC THROUGH INDEPENDENT ENGINEER. BUNDED AREAS | 1 | 5 | 2 | 2 | 20
14 | 32 | FOT- WASTE AREA & TRANSPORTATION WITHIN DPS | VARIOUS WASTE STREAMS STORAGE AREAS TRANSPORTATION EQUIPMENT SPILL KITS BUNDING CERTIFIED WASTE CARRIERS LEGISLATION | WASTE REMOVAL | 1. WASTE MANAGEMENT | ENVIRONMENTAL IMPROVEMENT CONSERVATION OF NATURAL RESOURES INCREASE LANDFILL SPACE REUSE, REDUCE, RECYCLE |  | ü | ü |  |  | ü | ü |  | ü | [19 empty] | 32 | [7 empty] | ü |  |  | WASTE MIXAGE DISORGANISED WASTE AREA | FOT AREA BEING DEVELOPED FOR WASTE MANAGEMENT | # LABELLED WASTE SKIPS REGULAR WASTE COLLECTION # DAILY CLEANING AND UPKEEP OF THE AREA # HIGHLEVEL SENSORS # BUNDED AREAS # OVERFLOW TO OILY WATER TANKS # REGULAR INSPECTIONS | 1 | 3 | 5 | 2 | 30
14U1 | 33 | FOT- WASTE AREA & TRANSPORTATION WITHIN DPS | VARIOUS WASTE STREAMS STORAGE AREAS | UREA SPILLS WASTE SPILLS | 2. EMISSIONS TO LAND 3. EMISSIONS TO AIR 4. WASTE MANAGEMENT 5. TRANSPORTATION 6. ODOUR 7.SPILLS | GLOBAL WARMING AIR POLLUTION WATER TABLE & SOIL POLLUTION ENVIRONMENTAL IMPROVEMENT CONSERVATION OF NATURAL RESOURES INCREASE LANDFILL SPACE REUSE, REDUCE, RECYCLE SEA POLLUTION DEPLETION OF NATURAL RESOURCES COMMUNITY AND HEALTH ISSUES DEGRADATION OF THE ENVIRONMENT DECREASED LANDFILL SPACE | ü |  | ü | ü | ü | ü | ü | ü | ü | ü | ü |  | ü | ü | ü | ü | [12 empty] | 33 | [8 empty] | ü |  | UREA AND WASTE SPILLS | HUMAN ERROR DAMAGED CONTAINMENT | # BUNDED AREAS # MANNED DURING TRANSPORTATION FOR TIMELY RESPONSE TO EMERGENCIES # SPADES TO CONTROL SPILL FLOWS THROUGH CULVERTS # OVERFLOW TO OILY WATER TANKS AND INTERCEPTORS #TRAINED EMPLOYEES AND SUPERVISION DURING WASTE COLLECTION # REGULAR INSPECTIONS | 1 | 6 | 4 | 6 | 144 | EASE SPILLS REMOVALFROM PIT THROUGH INSTALLATION OF PUMP. |  | Pump installation in waste area pit | OC 3
15 | 34 | STEAM AND CONDENSATE CYCLE | DEMINERALISED WATER TRUBINE PRESSURE DIRECTIVES | WATER BLOWDOWNS OUTLET TO SEA WATER | NA | [29 empty] | 34 | [13 empty] | 1 | 1 | 1 | 1 | 1
15U1 | 35 | STEAM AND CONDENSATE CYCLE | DEMINERALISED WATER TRUBINE PRESSURE DIRECTIVES | LEAKS EQUIPMENT DAMAGE DECREASED PERFORMANCE UNAVAILABILITY CHEMICALS | 1. ENERGY CONSUMPTION 2. EMISSIONS TO SEA 3. CHEMICALS | AIR POLLUTION SEA POLLUTION LAND POLLUTION DEPLETION OF NATURAL RESOURCES ENDANGERING ECOSYSTEM COMMUNITY & HEALTH ISSUES | ü |  |  |  | ü | [5 empty] | ü | ü | ü |  | ü | [13 empty] | 35 | [8 empty] | ü |  | INEFFICIENT SYSTEM | STEAM LEAK EQUIPMENT DAMAGE | AUDIBLE NOISE | 1 | 4 | 4 | 2 | 32
15U2 | 36 | STEAM AND CONDENSATE CYCLE | DEMINERALISED WATER TRUBINE PRESSURE DIRECTIVES | HAZARDS & EXPLOSIONS | 4. HS HAZARDS 5. NOISE | DIRECT EMPLOYEE HARM / INJURY COMMUNITY AND HEALTH ISSUES | ü | [13 empty] | ü |  |  |  |  | ü | [8 empty] | 36 | [9 empty] | ü | LEAKING PIPEWORK EXPLOSION |  | # CERTIFICATION OF SAFETY AND RELIEVE VALVES # ROUTINE VISUAL INSPECTION # SENSORS AND GAUGES ON DCS # AUDIBLE NOISE | 1 | 9 | 3 | 6 | 162 |  | DCS upgrade was made in 2019 | ATEX Certification planned 2021. Quotes, budgets and plans to be made in 2020. | OC 9
16 | 37 | SUPPLIES | UREA LUB OIL | UREA SUPPLY CONTAINERS FOR REUSE | 1. WASTE MANAGEMENT 2. TRANSPORTATION 3. BAT | ENVIRONMENTAL IMPROVEMENT CONSERVATION OF NATURAL RESOURES INCREASE LANDFILL SPACE REUSE, REDUCE, RECYCLE AIR POLLUTION SEA POLLUTION GLOBAL WARMING DEPLETION OF NATURAL RESOURCES |  | ü | ü |  | ü | ü | ü |  |  |  | ü |  | ü | ü | [14 empty] | 37 | [13 empty] | 0.5 | 5 | 2 | 2 | 10 | POSSILE USE IN CARS ABATEMENT, BY USING UREA TO BE SPRAYED ON CARS ABATEMENT. USE OF OUR FACILITY TO CREATE THIS EMISSION LOWERING INNOVATION IN CARS.
16U1 | 38 | SUPPLIES | UREA | LEAKAGE SUPPLY SHORTAGE | 4. ODOURS 5. AIR EMISSIONS 6. LEGAL BREACH 7. ENERGY CONSUMPTION | COMMUNITY & HEALTH ISSUES GLOBAL WARMING DEGRADATION OF ENVIRONMENT DECREASE IN LANDFILL SPACE WATER TABLE & SOIL POLLUTION ENVIRONMENTAL DETRIMENT STAKEHOLDER DETRIMENT, HARM OR INJURY AIR POLLUTION WATER TABLE & SOIL POLLUTION DEPLETION OF NATURAL RESOURCES | ü |  |  | ü | ü |  |  | ü |  | ü | ü |  | ü | ü | ü | ü | ü |  |  | ü | ü | ü | [6 empty] | 38 | [8 empty] | ü |  | NO UREA SUPPLY AND ABATEMENT OPERATION | LOGISTIC OR MANUFACTURING PROBLEMS | # LOCAL SUPPLIER MAINTAINS A CONSIDERABLE STOCK FOR D3PG. #AGREEMENTS IN PLACE TO COVER SAID SUPPLIES | 1 | 9 | 2 | 2 | 36 |  | 4CSR &1 ENV activities were organised in 2019
17 | 39 | CSR ACTIVITIES | [6 empty] | ü |  |  | ü | ü |  | ü | [8 empty] | ü |  |  | ü | [5 empty] | ü |  | 39 |  | ü |  |  |  | ü | [7 empty] | 1 | 4 | 4 | 2 | 32 | OFFEST OPERATIONS ENVIRONMENTAL IMPACT | 4CSR &1 ENV activities were organised in 2019
19 | 40 | GENERAL | FUEL PLANT ABATEMENT GENERAL OPERATIONAL IMPROVEMENT | EMISSIONS TO AIR & SEA COMPLAINTS BETTER PLANT EFFICIENCY | 1. NOISE 2. GLOBAL WARMING 3 BAT | COMMUNITY AND HEALTH ISSUES LOW IMPACT BAT |  | ü | [6 empty] | ü |  |  | ü |  | ü | ü |  |  | ü | ü |  | ü | [7 empty] | 40 |  |  | ü |  |  |  |  | ü |  |  | STAKEHOLDER COMPLAINTS SYSTEM INEFFICIENCIES | VARIOUS - TO INVESTIGATE AS APPLICABLE ON A CASE BY CASE BASIS | # ALL ENGINES ARE ENCLOSED IN NOISE ENCLOSURES BAT ABATEMENT # PROCEDURES IN PLACE :IMSP 14-01-NC & CA_1 NC, Investigation, CA & PA # SUPPORT FROM OEM | 1 | 8 | 9 | 5 | 360 | INVESTIGATION & RISK MITIGATION | Following IESC complaints of compressor overheating, BWSC investigated and provided possible recommendations reduce risk of overheating and increasing efficiencies. internal evaluation led to compressor ventilation improvement. | 5 of the compressor will be connected together to enable better load sharing improving system efficiency. • Compressors better load sharing would generate less compressor lube oil change requirements ( thus less waste ) in addition to better plant reliability | OC 10
20 | 41 | ENGINES | FUEL PLANT ABATEMENT | EMISSIONS TO AIR & SEA | 1. NOISE 2. GLOBAL WARMING 3 BAT | AIR POLLUTION GLOBAL WARMING DEPLETION OF NATURAL RESOURCES EMS LOW IMPACT BAT | ü |  |  |  | ü |  |  | ü |  |  |  |  | ü | ü |  |  |  | ü | [7 empty] | ü |  |  | 41 | ü |  |  | ü |  |  |  | ü |  |  | ENGINES STOP WORKING / MALFUNCTION ENGINES COMMUNICATION ISSUES | VARIOUS - TO INVESTIGATE AS APPLICABLE ON A CASE BY CASE BASIS. DCS CONNECTIVITY LOSS WITH ENGINE CONTROLLERS REQUIRING SWITCHING TO MANUAL MODE FROM LOCAL CONTROLLERS. DF ENGINES ON MANUAL MODE FORM LOCAL CONTROLLERS OPERATE ON GASOIL INSTEAD OF NATURAL GAS INCREASING AIR EMISSIONS. | # ALL ENGINES ARE ENCLOSED IN NOISE ENCLOSURES # NOISE MONITORING EVERY 3 YEARS #CONTINUOUS OPERATIONS MONITORING #EXPERIENCED MAINTENANCE CONTRACTORS (IESC & WARTSILA) AND ENGINEERS FOR TROUBLESHOOTING AND REPAIRS ON SITE. #CONVERSION TO LNG - REDUCES AIR EMISSIONS #PREVENTIVE MAINTENANCE # DSC NOT FUNCTIONING AND LOSS OF ENGINE CONTROL, WHICH IS RECTIFIED THROUGH ENGINE PANELS. | 1 | 5 | 8 | 8 | 320 | YEARLY PREVENTIVE MAINTENANCE PLAN EMISSION MONITORING REPORTING - MRA / ERA |  | DF ENGINES ON MANUAL MODE FORM LOCAL CONTROLLERS OPERATE NOW CAN OPERATE ON GAS RATEHR THAN GASOIL, HENCE IMPROVING EMISSIONS | OC 10
20U1 | 42 | ENGINES | FUEL PLANT ABATEMENT | EMISSIONS TO AIR & SEA | 1. NOISE 2. GLOBAL WARMING 3 BAT | AIR POLLUTION GLOBAL WARMING DEPLETION OF NATURAL RESOURCES EMS LOW IMPACT BAT | ü |  |  |  | ü |  |  | ü |  |  |  |  | ü | ü | [11 empty] | ü |  |  | 42 |  |  |  | ü |  |  |  |  | ü |  | - NO LNG AVAILABLE FOR D3PG | SHORTAGE OF LNG SUPPLY -FAULTY GAS SUPPLY EQUIPMENT (REGAS, GPRS ETC) | -DF ENGINES OPERATED ON GASOIL -AUTOMATED NOX ABATEMENT SYSTEM FOR GASOIL OPERATION IN PLACE -ERA COMMUNICATION ON FUEL CHANGE IN CASE OF LONG TERM GASOIL OPERATIONS '-COMMINUCATE WITH REWS, ENE & OTHER RELEVANT AUTHORITIES IN CASE OF REDUCED GENERATION CAPACITY - EMISSIONS ARE FULLY RECORDED AND WITH STIPULATED IPPC ELVS.AV48 | 0.5 | 7 | 3 | 2 | 21 | YEARLY PREVENTIVE MAINTENANCE PLAN ON GAS SUPPLY INFRASTRUCTURE.
20U1 | 43 | ENGINES | FUEL PLANT ABATEMENT | EMISSIONS TO AIR & SEA | 1. NOISE 2. GLOBAL WARMING 3 BAT | AIR POLLUTION GLOBAL WARMING DEPLETION OF NATURAL RESOURCES EMS LOW IMPACT BAT | ü |  |  |  | ü |  |  | ü |  |  |  |  | ü | ü | [11 empty] | ü |  |  | 43 |  |  |  | ü |  |  |  |  | ü |  | COMBUSTION FAILURE | VARIOUS | Combustion Failures on D3 plant would trip respective engines or else switch to alternative emergency fuel depending on engine type | 1 | 6 | 3 | 2 | 36 | YEARLY PREVENTIVE MAINTENANCE PLAN ON GAS SUPPLY INFRASTRUCTURE.
20U2 | 44 | ENGINES | FUEL PLANT ABATEMENT | EMISSIONS TO AIR & SEA | 1. NOISE 2. GLOBAL WARMING 3 BAT | AIR POLLUTION GLOBAL WARMING DEPLETION OF NATURAL RESOURCES | ü |  |  |  | ü |  |  | ü |  |  |  |  | ü | ü | ü | ü | ü | [7 empty] | ü | ü |  |  | 44 | ü |  |  | ü |  | ü |  |  |  | ü | MAJOR INCIDENTS / ACCIDENTS | VARIOUS - TO INVESTIGATE AS APPLICABLE ON A CASE BY CASE BASIS | # ALL ENGINES ARE SEPARATELY ENCLOSED IN FIRE SAFE ENCLOSURES. FIRE DOORS, FIRE ALARMS, GAS DETECTION SYSTEMS AND FIRE FIGHTING SYSTEMS. # FIRE SYSTEMS CERTIFICATION ON A YEARLY BASIS OR INACCORDANCE TO MANUFACTURER INSTRUCTIONS #CONTINUOUS OPERATIONS MONITORING #ERP #EMERGENCY TRAINED PERSONNEL #FIRST AID ROOM AND BOXES ON SITE #CPD STATION FOR DPS ONLY #ATEX CERTIFIED | 1 | 9 | 4 | 7 | 252 | #YEARLY FIRE FIGHTING SYSTEM CERTIFICATIONS #ERT | All carried out as required | #Argonite System 10 year certification. A major intervention will be carried out together with certification of 110 cylinders and pumps and valves replacement. System Testing will follow in 2021 . # OC 2 - Emergency Management | Aw
| 45 | [33 empty] | 45
#]

## ASPECTS & IMPACTS TABLE
Adverse / Offsets | SHARLENE | ASPECTS | IMPACTS | Comments
A | Solid Waste | WASTE | DECREASE IN LANDFILL SPACE DEGRADATION OF ENVIRONMENT WATER TABLE & SOIL POLLUTION GLOBAL WARMING
A | Air emissions | DUST | COMMUNITY & HEALTH ISSUES AIR POLLUTION
A | Nuisance | NOISE | COMMUNITY & HEALTH ISSUES
A | Air emissions | ODOUR | COMMUNITY & HEALTH ISSUES
A | Nuisance | VIBRATIONS | DEGRADATION OF ENVIRONMENT
A | Nuisance | VISUAL | DEGRADATION OF ENVIRONMENT
A | Air emissions | EMISSIONS TO AIR | GLOBAL WARMING AIR POLLUTION |  | No effluent discharge is connected to sewers or intentionally discharged in sea water
A | Hazardous material usage | EMISSIONS TO LAND | WATER TABLE & SOIL POLLUTION
A | Hazardous material usage | EMISSIONS TO SEA | SEA POLLUTION COMMUNITY & HEALTH ISSUES
A | Effluent discharges | EFFLUENT DISCHARGE | DEGRADATION OF WATER
A | Hazardous material usage | SPILLS | DEGRADATION OF ENVIRONMENT DECREASE IN LANDFILL SPACE WATER TABLE & SOIL POLLUTION
O | Solid Waste | REUSE, REDUCE, RECYCLE | ENVIRONMENTAL IMPROVEMENT CONSERVATION OF NATURAL RESOURES INCREASE LANDFILL SPACE REUSE, REDUCE, RECYCLE | The waste created by the plany operations is streamed in line with legal obligations and targeted for as much recycling as possible
A | Raw material usage | RESOURCES | DEPLETION OF NATURAL RESOURCES GLOBAL WARMING
O | Planned Offestting Initiatives | INITIATIVES | ENVIRONMENTAL IMPROVEMENT | Any environmental initiatives taken by the company to offset negative environmental impacts, inclusive of any possible influence to improve process impacts eg: packaging, transportation, supplier certifications, adherence to legislation, material improvement, recycling and reusing of products and packaging. Other activities include beach cleaning, tree planting etc.
A | Hazardous material usage | CHEMICALS | COMMUNITY & HEALTH ISSUES AIR POLLUTION STAKEHOLDER HARM / INJURY
O | Air emissions | BAT | LOW IMPACT BAT EMS BAT are the techniques with the lowest impact on the environment without compromising the economic health of the (industrial) enterprises concerned. It should be noted that Best Available Techniques refers to operational as well as technological factors and can include (but are not limited to) any or all of the following: *staff qualifications; * working methods; *training; *supervision; * design; *construction and maintenance; *design of plant and equipment; * monitoring and analysis. | Maintenance activities have a direct effect on the environment that surrounds the facility where they are executed. Long Life cycle machinery impact of in-use service as ell as maintenance have a significant importance. The effects of maintenance on the environment include: *Waste - Soild and Liquid *Fuel Consumption & efficiency *Engine Lifecycle (in terms of material and resources) * Controlled / reduced emisisons Environmental impact is limited through * Checks to ensure efficeint and effective limitation of environmental impact *Appropriate training *EMS procedures
A | Energy usage | ENERGY CONSUMPTION | AIR POLLUTION SEA POLLUTION WATER TABLE & SOIL POLLUTION DEPLETION OF NATURAL RESOURCES
A | Air emissions | TRANSPORTATION | AIR POLLUTION SEA POLLUTION GLOBAL WARMING DEPLETION OF NATURAL RESOURCES | Transportation at D3PG is limited to raw material acquisition. (indirect)
O | Energy usage | ENERGY CONSERVATION | CONSERVATION OF NATURAL RESOURCES REDUCED AIR POLLUTION | Any initiative taken to encourage energy conservation and offset environmental impact

## OTNOC - BREF
ITEM REF | OTNOC BREF Clause | Comments | FMEA Reference 2
3.1.16 Other than normal operating conditions (OTNOC)
To reduce emissions during other than normal operating conditions (OTNOC), a management
plan may be set up and implemented as part of the environmental management system, along
with the implementation of traceable concrete measures commensurate with the type of possible
OTNOC. These measures include:
1 |  appropriate design of systems considered to cause OTNOC and that may have an impact | Start and stops of engines are performed according to dispatche requirements, however, when frequent start an stops are required on D3Plant the practice is to start and stop as much as practically possible the same engines in order to maintain almost steady state temperatures on exhaust pipework and equipment. Such operational strategy would allow NOx abatement systems on respective engines to kick in just a few minutes after engine start. On cold engines NOx abatement function would start at a later stage once exhaust steady state temperatures are reached. | FMEA ENTRY 2
on emissions (e.g. low load design concepts for reducing the minimum start-up and
shutdown loads for stable generation in gas turbines);
2 |  drawing up of specific preventive maintenance plans for these relevant systems | Preventive Plans are drawn according to OEM manuals for engines and all auxiliary equipemnt in addition : -Plant is manned on a 24 by 7 basis so as to monitor and attend at the earliest any malfunction. - Strategic spares are kept stored on site so as to avoid any waiting time to perform repairs -On planning plant dispatch we tend to keep one or two engines on stand by so that we can swap engines in service in case there is a malfunction on one of the running engines. | FMEA ENTRY 5
3 |  review and recording of emissions caused by OTNOC; | Emissions are continuously recorded during start ups and shut downs through CEMS.
4 |  implementation of corrective actions to return to normal operating conditions (NOC); | Linked to item 2 | FMEA ENTRY 5
5 |  periodic assessment of overall emissions during OTNOC (e.g. frequency of events, | In line with IPPC requirements
duration, emissions quantification/estimation) and implementation of corrective actions if
6 | Monitoring of emissions during OTNOC is important as high pollutant emissions may occur | CEMS monitoring covers all instances and occurrences in line with IPPC
during these periods. Some countries include emissions monitoring provisions in environmental
permits.
7 | There may be cases in which alternative monitoring is more precise than direct emissions | CEMS is calibrated and can read even emissions produced with diesel opertations and without urea injection system finction for NOx abatement
measurement, e.g. monitoring based on surrogate parameters if the monitoring device is not well
calibrated in the range of emissions. Using emissions arising from a typical OTNOC as the basis
for assessing the emissions of each OTNOC is also a possibility as long as these OTNOC can be
linked by quantifiable parameter(s).
Other OTNOC
It is important to identify other than normal operating conditions as they may affect the level of
emissions or consumption of the combustion plant. The following situations are examples of
conditions that may be considered OTNOC:
8 |  periods related to malfunction or breakdown of the abatement techniques; | Review Item 7 Exhaust Path and abatement | FMEA ENTRY 13 - 17
9 |  testing periods (e.g. commissioning periods, periods after modifications to the | Review Item 7 Exhaust Path and abatement
combustion chamber, or testing periods of new/repaired abatement techniques or of the
combustion of a new fuel);
10 |  periods corresponding to the use of emergency fuels for a very short period due to the | Refer to entry 41 | FMEA ENTRY 42
lack of availability of normally used fuels (serious shortage or sudden interruption) or to
disturbances in fuel feeding;
11 |  periods of exceptional low-load operations due to unplanned malfunction of plant systems | Not applicable to D3Plant since it is composed of 8 small engines that are kept above 80% during operation.
12 |  periods related to sudden major combustion failures; | Combustion Failures on D3 plant would trip respective engines or else switch to alternative emergency fuel depending on engine type | FMEA ENTRY 43
13 |  periods related to malfunction of the auxiliary or monitoring systems (e.g. malfunctioning | Linked to item 2 | FMEA ENTRY 5
of the analysis instrument or data transfer related to the process control);
14 |  periods of calibration of monitoring systems requiring measurement points outside the | CEMS is calibrated and can read even emissions produced with diesel opertations and without urea injection system function for NOx abatement
range corresponding to normal operating conditions;
15 |  extraordinary/unforeseeable variations in fuel quality whereby the installation/equipment | If fuel quality does not abiade by contract conditions D3PG has the right to refuse to dispatch respective engines using such non-conforming fuel. Leading to No LNG Availability Item. | FMEA ENTRY 42
performance cannot be guaranteed by the manufacturer (outside design specifications)
and/or where there is a failure in the application of the fuel quality check procedures;
16 |  in the case of bypass of control equipment or a process, when the bypass is unavoidable, | Not applicable
e.g. to prevent loss of life or personal injury.
| BAT 10. In order to reduce emissions to air and/or to water during other than normal | In place
operating conditions (OTNOC), BAT is to set up and implement a management plan as
part of the environmental management system (see BAT 1), commensurate with the
relevance of potential pollutant releases, that includes the following elements:
 appropriate design of the systems considered relevant in causing OTNOC that
may have an impact on emissions to air, water and/or soil (e.g. low-load design
concepts for reducing the minimum start-up and shutdown loads for stable
generation in gas turbines);
 set-up and implementation of a specific preventive maintenance plan for these
relevant systems;
 review and recording of emissions caused by OTNOC and associated
circumstances and implementation of corrective actions if necessary;
 periodic assessment of the overall emissions during OTNOC (e.g. frequency of
events, duration, emissions quantification/estimation) and implementation of
corrective actions if necessary.