## Title Page
DPS Bund register
| Title | DPS Bund register
| Reference | EGM-HSE-EMR-13
| Date of latest update | 14th May 2020
| Revisor | Matthew Grech
| Reviewers | Michael Sant
| Approver | Jani Kerænen
Revision History
|  | Date | Change |  | Revisor
|  | May 2020 | updated with column of certificte dates |  | MG

## Bunds
DPS Bunds
|  | Tank Description | KKS Number | Location | Tank Capacity in m3 | Bund Capacity in m3 | Bund/Tank Boundary Wall Type | Bund/Tank Boundary Wall Thickness | Date | Certificate Number
ESBi | 1 | Ammonia dosing skid tank | 50ULA | Under boiler HRSG53 | 0.5 | 0.55 | S/S | 1mm | 2019-12-06 | 19-609-04
ESBi | 2 | Phosphate dosing skid tank | 50ULA | Under boiler HRSG53 | 0.5 | 0.55 | S/S | 1mm | 2019-12-06 | 19-609-05
ESBi | 3 | Hydrochloric Acid dosing skid tank | 50UGE | Polishing Plant Dosing Container | 0.2 | 0.22 | PTFE | 1mm | 2019-12-06 | 19-609-06
ESBi | 4 | Steam Turbine control oil and Steam Turbine lubricating oil | 50UMA04 | Steam turbine oil skid | 10.635 | 11.6985 | Reinforced Concrete | bottom 1600mm side 500mm | 2019-12-06 | 19-609-07
ESBi | 5 | Gas Turbine GT51 lubricating oil tank | 51UMB01 | GT51 compartment | 10 | 11 | Reinforced Concrete | - | 2019-10-06 | 19-609-03
ESBi | 6 | Gas Turbine GT52 lubricating oil tank | 52UMB01 | GT52 compartment | 10 | 11 | Reinforced Concrete | - | 2019-10-04 | 19-609-01
ESBi | 7 | Gas Turbine GT53 lubricating oil tank | 53UMB01 | GT53 compartment | 10 | 11 | Reinforced Concrete | - | 2019-10-04 | 19-609-02
ESBi | 8 | Oil filled step up transformer ST | 50BAT10 | 50UAB | 26.875 | 29.5625 | Reinforced Concrete | bottom 400mm side 250mm | 2019-11-27 | 19-609-08
ESBi | 9 | Oil filled step up transformer GT51 | 51BAT10 | 51UBF | 45 | 49.5 | Reinforced Concrete | bottom 400mm side 250mm | 2019-11-27 | 19-609-09
ESBi | 10 | Oil filled step up transformer GT53 | 53BAT10 | 53UBF | 25 | 27.5 | Reinforced Concrete | bottom 400mm side 250mm | 2019-12-06 | 19-609-10
ESBi | 11 | Oil filled auxiliary transformer GT51 | 51BBT10 | 51UBE | 6.67 | 7.337 | Reinforced Concrete | bottom 400mm side 250mm | 2019-12-06 | 19-609-11
ESBi | 12 | Oil filled auxiliary transformer GT53 | 53BBT10 | 53UBE | 6.67 | 7.337 | Reinforced Concrete | bottom 400mm side 250mm | 2019-12-06 | 19-609-12
ESBi | 13 | Oil Interceptor | 50UBH | Oil Interceptor Pit | 15.6 | No Bund | GRP | 7mm | 2020-11-08 | ESBI/01/2020
Reganosa | 1 | WG Pumps | 12 PGA40/30 AP001 | WG | 1 | 36.4 | Concrete | 0.2 m | 2019-09-26 | MG/RP/09162
Reganosa | 2 | Expansion Vessel 1 | 12PUN10 BB002 |  | 5
Reganosa | 3 | Temporaly WG Tank | - |  | 10
Reganosa | 4 | Expansion Vessel 2 | 12PUN10 BB003 | WG | 5 | 3.2 |  |  | 2019-09-29 | MG/RP/09167
Reganosa | 5 | BOG Compressor No1 | 12EKH10AN001 | BOG | 0.38 | 1 | Reinforced Concrete | 0.1 m | 2018-08-26 | 18-606-03
Reganosa | 7 | BOG Compressor Lube Oil |  |  | 0.956
Reganosa | 8 | BOG Compressor No2 | 12EKH20AN001 |  | 0.38 | 1 | Reinforced Concrete | 0.1 m | 2018-08-27 | 18-606-03
Reganosa | 10 | BOG Compressor Lube Oil |  |  | 0.956
Reganosa | 11 | BOG Compressor No3 | 12EKH30AN001 |  | 0.38 | 1 | Reinforced Concrete | 0.1 m | 2018-08-28 | 18-606-03
Reganosa | 13 | BOG Compressor Lube Oil |  |  | 0.956
Reganosa | 14 | Impouding Basin | - | Impouding basin | 15.75 | 400.5 | Reinforced Concrete | 0.20 m | - | -
Reganosa | 15 | NVCC KO Drum | 12EKR10BB001 | NVCC KO Drum | 360.36
Reganosa | 16 | FF Sea Water Diesel Tank | 12SGA20BB001 | Sea Water Pumps | 2.08 | 3.85 | Reinforced Concrete | 0.20 m | 2018-08-26 | 18-606-04
Reganosa | 17 | FF Sea Water Diesel Pump | 12SGA20AP001 |  | 0.049
Reganosa | 18 | Jetty Platform | - | Jetty | - | 21.92 | Reinforced Concrete | 0.2 m | 2018-08-26 | 18-606-01