Appendix I: Comments regarding the information submitted as part of Annex 1-10 of the application

| Reference to Section of the Renewal Application | ERA Review 06-02-2019 | Wasteserv’s Reply 14.03.2019 | ERA Review 15-04-2019 | Wasteserv’s Reply 31.07.2019 |
| --- | --- | --- | --- | --- |
| Introduction and Scope of the application | Applicant is to submit a plan showing how this activity compares with the latest National Waste Management Plan required by The Waste Regulations, S.L. 549.63 and calculations therein. - Operator shall indicate how the following requirements of the Landfill Regulations shall be achieved: - An increased level of pre-treatment of waste prior to landfilling including but not limited to plans with time-frames of changes to the operations at the Malta-North MBT. - How the most appropriate treatment option and adequate selection of waste streams shall be applied prior to landfilling. - Stabilisation of the organic fraction of the waste to be landfilled. - Kindly re-submit a general site plan clearly marking (and labelling) all areas within the installation to provide: - a more clear understanding of the status of infilling of the landfill highlighting areas with remaining void space, - the amount of void space (and remaining lifetime) in each area, and differentiating between pre-settlement and post-settlement profiles for both the existing permitted landfill. | The National Waste Management Plan required by The Waste Regulations, S.L. 549.63 sets various targets for waste management that aim ‘to reduce the generation of waste and to increase source separation so as to promote recycling and reduce landfilling’. Wasteserv has implemented various management and infrastructure projects – that are not within scope of this IPPC permit - that are aimed towards achievement of the above targets. In this regard, this application for renewal aims to preserve the remaining void space within the Zwejra landfill for emergency purposes, and commence the process for the partial capping of the facility. The development permit process for the final structure is planned for 2019. - The Malta North plant and the Sant Antnin MTP are the pre-treatment being applied to the waste prior to landfill. Given the accident at Sant Antnin, treatment capacity has been compromised, with the result that pre-sorting of wastes prior to landfilling is not carried out for all landfilled wastes. The shortfall in capacity needs to be considered in the context of current initiatives to divert recyclables and biodegradable wastes away from landfill. It is expected that the upcoming update to the national waste management plan – due to expire in 2020 – shall include further measures to deviate further volumes of such wastes away from landfill, from both the municipal and industrial sectors. Development of the plan, in conjunction with current plans for further expansion at Malta North, are essential for the definition of the capacity needed, as is a clearer definition of the required phasing of the Sant Antnin decommissioning; the above are expected to be presented for endorsement through established procedure. A combination of increased treatment capacity, facilitated by current initiatives for segregated collection of biodegradable wastes, are considered sufficient for stabilisation of the organic fraction of wastes prior to landfill. - A site plan is attached as Annex A. This includes an outline cut and fill design which has been commissioned in preparation for the eventual landfill capping development permit process. This cut and fill exercise is indicative of the pre-settlement contours. The closure plan submitted provides generic details as regards the projected capping, which will need to be updated through the setting of contractor design specifications in parallel with the development permitting process. This will be included within the application for surrender of the facility. The cut and fill will involve shifting of daily cover material and inert stockpiles generated during the original excavations, and recontouring of the wastes where required. The latest survey data indicates a remaining void space of circa 27,000 cubic metres. | - Noted. - ERA notes that further details particularly on closure monitoring will be included in the final closure plan that shall be submitted in 2019 and subject to any other requirements from other Authorities. To however note that although the closure and after-care process will be addressed at a later stage, the Authority shall only consider permit surrender applications when the Authority is satisfied that all the obligations of S.L. 549.29 including monitoring would have been addressed. Annex A indicates that on several areas, the permitted pre-settlement height appear to be exceeded with the current height of the waste mass. With reference to the complete closure plan required by this review, applicant is to clarify whether the thickness/height of the capping and any associated infrastructure is being considered within the post-settlement heights. Operator is to provide time-frames by when the cut-and fill exercise is expected to obtain the height contours permitted in IP 01/05/B. | / Noted. The area where height has been exceeded is a soil stockpile, reserved for use in the rehabilitation of the same landfill. Thickness / height of the capping and any associated infrastructure is considered within the post-settlement heights, or as may be required within the development permit application to be submitted for the final restoration. A preliminary estimate is that all cut & fill works will be concluded in 18 months. |
| Annex 1 | No. 15 - Inspection and Maintenance contract: - With reference to Annex 2 of the IPPC renewal application of Ghallis non hazardous landfill, kindly clarify what the updated management practices consist of which would supersede the inspection and maintenance contract. No. 24 - Submission of environmental management system (EMS): - The submitted EMS refers only to Ghallis non-hazardous landfill covered by IP 0001/06. Kindly resubmit EMS to refer to Ta’ Zwejra non-hazardous engineered landfill facility and address the below issues: - Operator is to submit a copy of the “MEC QP04 Waste Processing Procedure” with details of how such document is managed in accordance with section 6 (Records) of the “MEC EP 03_Non-hazardous…” document. Applicant is to clarify whether this is the same document submitted as part of the EMS and referred to as “MEC QP01 ….”. This document is to indicate that the tip face controller shall do the necessary checks to ensure that no unauthorised waste is landfilled and take the required actions accordingly including but not limited to the removal of unauthorised waste to appropriate designated area and keeping of such records. Similarly details of how these documents : “Controlled Document 103a Environmental Monitoring Programme for the Non-Hazardous Engineered Waste Landfill at” and “Għallis Controlled Document 103c Għallis & Zwejra Monitoring Plan” are being managed, is also required. - With reference to “MEC EP 06 Leachate Management”, operator is to indicate how the temporary leachate collection points shall be designed in a manner to be away from the cell liner’s edge and in a manner to prevent contamination to the surrounding environment. - With reference to “MEC QP01 Waste Processing Procedure”, operator is to indicate how the daily cover will be removed at the start of daily operations at the tipping face. No. 25 - On-site leachate treatment system. the data submitted in the Annual Environment Reports indicates repeated exceedances of the following control and trigger levels: - Arsenic - Cadmium - Chromium - Copper - Nickel - Lead - Ammoniacal Nitrogen - Chloride This may indicate that current practice of recirculation of leachate is not conducive to the achievement of the required levels. To this end please submit a proposal with time-frames for leachate treatment including clearances from relevant Authorities/Departments and in accordance with Waste Management (Landfill) Regulations S.L. 549.29. Furthermore, operator is to trigger the contingency plan for any such exceedance including but not limited to the execution of a series of actions to further analyse, identify the source, and control the situation to rectify the levels of that particular pollutant. Since according to letter from applicant dated 10th October 2018, negotiations for the leachate treatment with WSC seem to be unfeasible (Task A), operator is to submit to ERA the initial leachate management report for further assessment and consultation with other competent entities. Above comment on project phasing and timing refers. No. 26 – Risk assessment to determine whether a gas drainage layer is necessary as part of the proposed surface sealing (capping system). Should the applicant intend to retain part of the tip-face uncapped in case of emergency, applicant is advised to submit a development permit application with a plan (with drawings and time-frames) for the phased capping of the Zwejra landfill; in which capping shall commence in the areas which no longer have void space remaining and provide a risk assessment for such areas. This was already requested through ERA’s letter dated 20th June 2016, in view that the landfill commenced operations in 2005 but effectively has received very little waste inputs since 2008. In this regards any required development permit applications are to be submitted to the Planning Authority for consideration. With reference the submitted Closure plan in Annex 4: - Plans and sections referred to in the document are to be provided. - A clarification on whether soils will be landfilled as part of the capping system, noting the requirements of Fertile Soil (Preservation) Act of 1973. - It does not include any reference to either risk assessment for a drainage layer requested in No. 26 or a proposal on the maintenance, monitoring and control requested in No. 27. No. 27 - Proposal on the maintenance, monitoring and control in the aftercare phase of the site It is being understood that the operator is proposing that this item is combined with No. 26 above. Whilst this is acceptable for the Authority, this shall be submitted as part of this renewal application and as required by S.L. 549.29 – Waste Management (Landfill) Regulations. No. 28 - Submission of a monitoring programme proposal for site surface runoff collected by the silt trap & reservoir Submitted document has been assessed and consolidated feedback on all monitoring proposals therein has been provided through the Compliance and Enforcement process. | No. 15 An Inspection & Maintenance procedure (MEC EP08) is attached in Annex B. No. 24 The omitted reference to the Zwejra landfill is being corrected via a change in scope of the EMS. - The reference to QP01 was a typographic error that has been corrected in the attached version. “Controlled Document 103a Environmental Monitoring Programme for the Non-Hazardous Engineered Waste Landfill at” and “Għallis Controlled Document 103c Għallis & Zwejra Monitoring Plan” highlight the procurement processes for environmental monitoring services. - Given that the lines have been laid down and all leachate collection points are distant from the liner edge, this matter is no longer considered to be a risk. As a consequence, procedure MEC EP 06 Leachate Management becomes redundant. - Daily cover is removed by mechanical means. No. 25 Wasteserv is currently in the process of identifying the technologies required for treatment of leachates. To this end, the following study SLR (2016) Ghallis Non Hazardous Landfill: Leachate Management and Disposal Options Report was commissioned to determine the options that were available. Consideration of the leachate parameters highlighted the need for more detail with respect to the design of appropriate leachate treatment solutions, with the result that Ing. Marco Cremona has been contracted to assist in the identification of solutions that will result in pilot trials. Permitting processes related to leachate treatment infrastructure are planned for 2019, with initial pilot trials being scheduled for 2020. No. 26 A development permit application is being developed for submission during 2019 as suggested, allowing for the partial capping, leaving an exposed tip face (which shall act as back-up tipping spot in case of an emergency). - Closure plans and sections are attached. - No soils will be landfilled; soils present on site are materials that had been used as cover. - The closure plan submitted provides generic details as regards the projected capping, which will need to be updated through the setting of contractor design specifications in parallel with the development permitting process. This will include the calculation and design of the appropriate thickness of the drainage layers. No. 27 The closure plan submitted provides generic details as regards the projected capping, which will need to be updated through the setting of contractor design specifications in parallel with the development permitting process. This will be part of the application for surrender of the facility. The maintenance, monitoring and control processes will be derived from the contractor design specifications, and will be incorporated within the facility EMS, as will be specified within the application for surrender of the facility. No. 28 Monitoring of the silt trap and reservoir are being added to the Environmental Monitoring Programme currently under review by ERA. | No. 15 With regards to Annex B, kindly provide further details on the instrumentation and methodology used to detect landfill gas leaks making reference to any recognised national/foreign standard or guidance. No. 24 Whilst noting the clarification provided in relation to the procurement process, ERA query No. 3a) regarding improvement program item No. 24 and associated document management is still to be addressed. No. 25. Whilst noting the submitted study covering leachate at Ghallis landfill, in view that leachate recirculation is increasing pollutant concentration over time, applicant is to propose an alternative leachate treatment/disposal system by the end of 2019 for implementation in year 2020. No. 26. As part of this renewal permit, the submission of a complete closure plan will be required by December 2019. No. 27 The closure plan is an integral part of the operational IED permit, which permit may only be surrendered after the Authority is satisfied that all closure and aftercare has been carried out as required according to the processes and time-frames required by S.L. 549.29. No. 28 Noted. | Testing of landfill gas remains as stipulated in the approved EMP, as may be amended from time to time (subject to ERA approval). Annex B involves a visual inspection (as per procedure MEC EP08) & hence no equipment is used. Inert material is used to mitigate these gas leaks which usually are present due to a crack in the ground due to combustion occurring beneath the ground. See Annex 5. Noted. Noted. Noted. / |
| Annex 3 | With reference to the Annual Environmental Report obligations of the expired IPPC permit, applicant to note that following previous communications that the following monitoring data for year 2017 the below clarifications/submissions are still to be provided : Landfill Gas Monitoring - Surface emissions: missing for LFG 1, LFG 2, LFG 3, LFG 5, LFG 9 and LFG 11. - Groundwater Monitoring: missing for MBH5 and BH 00574. - Leachate Gasses: CO & O2 exceedances for all collection points. Groundwater Analysis - Groundwater Monitoring: MBH5 and BH 00574 missing. Alternative monitoring points are to be proposed as part of a revised Monitoring Programme. - Exceedances for Ammoniacal nitrogen in BH 4 and Cadmium for all boreholes. Surface Water Analysis Quarterly average exceedances in: Ammonical Nitrogen: All SWs Arsenic: SW1 & SW3 Cadmium: All SWs Chromium: SW1 & SW3 Nickel: All SWs Lead: All SWs In view that water from the run-off collection points is to end up into the groundwater through infiltration, it is of high importance that alternative groundwater monitoring points are proposed instead of those referred to above and in the vicinity of the surface water collection points. Leachate monitoring In view of the reported exceedances in the following parameters: Arsenic: LCP Z4 & Z5 Cadmium – LCP Z3 & Z6 Chromium – All LCPs Copper – LCP Z2, Z3 ,Z5 & Z6 Nickel – LCP Z5 Lead – LCP Z3, Z5 & Z6 Ammoniacal Nitrogen – LCP Z3 ,Z4 & Z6 Chloride – LCP Z1, Z2, Z3, Z5 & Z6 above comment in Annex 1 (No. 25) concerting leachate treatment refers for further submissions. WSM is to ensure that monitoring is carried out as per the latest approved Environmental Monitoring Programme and to provide justification for the missing data especially for landfill gases and groundwater analysis Operations on Site during Inspection From Action 1, Task A of the operator’s letter dated 18th October 2018, it is being understood that all the recyclable waste shall be exported for treatment by July 2019. As per Regulation 9(1) of The Waste Regulations, S.L. 549.63, no mixing of grey bags with other waste of different nature is permitted at Ta’ Zwejra landfill. Should applicant intend to propose such storage and/or associated handling, this shall be declared to the Authority so as to allow it to evaluate whether the proposal can be implemented through an IPPC variation application. Area above water reservoir Applicant is to submit an updated stock and concrete plan of how the remaining waste streams which are not destined for the local landfills shall be disposed of. This shall include photographic evidence of how the current stock is securely kept to reduce the risk of combustion and being blown away by the wind. Should this use of such area be retained as is, applicant is to submit an updated layout plan and method statement showing the maximum capacity of such waste together with a description of how it shall be safely and securely stored. Remaining Void Space Above comments on items 26 and 27 of the Improvement Program refer. Leachate Management Above comment in Annex 1 No. 25 refers. The applicant can choose to include such a plan with that for the Ghallis landfill or submit a separate one. In the case of the former, this shall be submitted as part of this renewal application. | The Environmental Monitoring Programme for the Maghtab Environmental Complex is currently under review by ERA, to be updated as required. Proposed updates include: - Resumption of surface landfill gas monitoring for those points which had been omitted due to administrative oversight; - Replacement of groundwater monitoring points for those boreholes which are no longer accessible due to third party development projects (Coast Road), or lack of permission from third parties to access their land; - Rationalisation of surface water quality monitoring to monitor the silt collection pond and reservoir, as being more representative of surface waters on site rather than puddles of water on the waste mass. It should be noted that the exceedances for ammoniacal nitrogen is likely to be due to the presence of animal farms in the surrounding areas, and past episodes of illegal dumping of animal wastes in the surrounding fields. Similarly, Cadmium has been known to be a contaminant of NPK mineral fertilisers. It is recommended that the future update of the EMP considers the possibility of evaluating external sources of pollution that may affect monitoring results, as well as legacy pollution (i.e. the Maghtab landrise), to establish a clearer trends in the monitoring results. Noted. Photographs attached demonstrate how this area has been cleared. See previous comments See previous comments | Whilst noting the below justification for Ammoniacal Nitrogen, kindly note that justifications for the other missing monitoring results or exceedances have not been provided. Should applicant consider it necessary to monitor external sources of pollution, these are to be included in the revised EMP together with any associated access agreements with third parties. Noted Noted Noted Refer to previous comments and below feedback from Regulatory Consultees regarding Leachate Treatment proposal. | The monitoring data does not provide clear trends either spatially or temporally. Leakage of leachate would result in higher levels of pollution more comparable with leachate parameters and levels. Alternative pollution from other sources cannot be excluded e.g. fertilisers using phosphorus additives from North Africa tend to be contaminated with Cadmium. Similarly, mobilisation of pollution from the old Maghtab landrise cannot be excluded. In this regard, a wider baseline study of the entire valley system would be required. / / / See other sheet (with feedback from consultees). |