## Maintenance Plan
2016
Equipment Reference | Section | Machine / Area |  |  | Frequency | Last Maintenance | Records | January |  | February |  | March |  | April |  | May |  | June |  | July |  | August |  | September |  | October |  | November |  | December
[8 empty] | Planned | Carried Out | Planned | Carried Out | Planned | Carried Out | Planned | Carried Out | Planned | Carried Out | Planned | Carried Out | Planned | Carried Out | Planned | Carried Out | Planned | Carried Out | Planned | Carried Out | Planned | Carried Out | Planned | Carried Out
| General MTP/AD - Site Cleaning | MBT 1, 4 and 5 containers |  | Floor | 1 Week
|  | CHP Container |  | Floor | 1 Week
|  | CHP Container |  | Exterior Panels and Equipment | 1 Week
|  | RTO & Gas Booster Container |  | Floor | 1 Week
|  | RTO & Gas Booster Container |  | Control Room | 1 Week
|  | RTO & Gas Booster Container |  | Equipment (Pumps, Pipework etc. - detailed below) | 1 Week
|  | Site Laboratory |  | Floor | 1 Day
|  | Site Laboratory |  | Rubish bin (including general clean up) | 1 Day
|  | Site Control Room |  | Floor | 1 Day
|  | Site Control Room |  | Rubish bin (including general clean up) | 1 Day
|  | Digester Pit (Summer Period) |  |  | 1 Week
|  | Digester Pit (Winter Period) |  |  | 2 Days
|  | AD Area |  | Floor (RTO area, gas bubble area, RO area etc.) | 2 Days
|  | AD Area |  | Equipment (Pumps, Pipework, motors, safety signs, dosing cabinets etc. - detailed below) | 1 Month
|  | AD Area |  | Walkways on Aeration and Digester Tanks | 1 Week
|  | Compost Shed |  | Thorough cleaning | 1 Week
|  | Compactors Area |  | Thorough cleaning | 1 Week
|  | Roads surrounding AD Area |  |  | 2 Days
|  | Receiving Area |  | Thorough cleaning of Receiving Area | 1 Week
|  | Dry MTP |  | Thorough cleaning | 1 Week
|  | Dry MTP |  | Daily Plant cleaning after end of operation | 1 Day
|  | Wet MTP |  | Floor | 2 Days
|  | Wet MTP |  | Cesspits | 2 Days
|  | Wet MTP |  | Walkways | 2 Days
|  | Wet MTP |  | Exterior Mixer | 1 Week
|  | Wet MTP |  | Indoor and outdoor conveyors | 1 Week
|  | Wet MTP |  | Pumps, Pipework and compressor unit - detailed below | 1 Week
|  | Wet MTP |  | Incoming organic hopper | 1 Day
|  | Dewatering building |  | Floor | 2 Days
|  | Dewatering building |  | Equipment (Pumps, Pipework, motors, safety signs, dosing cabinets etc. - detailed below) | 2 Days
|  | Dewatering building |  | Flocculation stallion and tank | 2 Days
|  | Dewatering building |  | Decanters | 1 Week
| Dry MTP - Fast Roller Shutter | Fast rolling shutter |  | Clean the structure, photocells, radar and hatches with damp cloth without using any solvent | 6 Months
| Dry MTP - Air Curtain | Air curtain | TTF Engineer | Clean out the water heat exchanger and the inside of the air curtain using a fine hand brush or vacuum cleaner | 2 Months
|  | Air curtain |  | Clean the case of air curtain using a cloth with soapy water | 2 Months
| Dry MTP - Bag Opener | Ripping drum | TTF Engineer | Clean outer and inner drum side; remove wound up materials | 1 Week
|  | Hydraulic unit |  | Clean oil filter | 1 Month
|  | Hydraulic unit |  | Clean ventilation filter | 1 Month
|  | Moving floor |  | Remove dust and dirt from bottom side of moving floor | 3 Months
|  | Moving floor |  | Clean pistons | 3 Months
|  | Electrical equipment |  | Clean interior of the switch box | 1 Month
| Dry MTP - Belt Conveyor | Belt conveyor |  | Remove material adhered to the supports of belt in order to avoid locking of the rollers | 1 Week
|  | Belt conveyor |  | Clean the conveyor, remove deposits such as dust or conveyed material, particularly from walkways; | 1 Week
| Dry MTP - Electromagnetic Belt Separator | Magnetic belt |  | Clean drums and rollers | 1 Year
|  | Motor |  | Clean the cooling air passages | 5 Years
| Dry MTP - Eddy Current Separator | Eddy current separator |  | Clean the polar wheel | 1 Week
|  | Motor of polar drum |  | Clean the cooling passages through which cooling air flows | 3 Months
|  | Drive motor |  | Clean the cooling air passages | 2 Years
|  | Fan of polar drum |  | Remove dust from grille of fan | 6 Months
| Dry MTP - Rotary Screen | Rortary screen |  | Clear out the discharging hopper under the rotary screen | 1 Week
|  | Motor |  | Clean the housing, air-flow channels and guard of fan | 1 Year
| Dry MTP - Weighing Scale |  |  | Clean between load cells and the belt for any material ingress between these two points | 2 Weeks
| Dry MTP - Compactor | Compactor |  | Clean out any waste material that has generated behind the ram and also within the compactor body | 1 Day
| Dry MTP - Suction Cycle Blower | Fan |  | Clean internal parts (casing and nozzles) from dirt residues and remove any foreign bodies; | 3 Months
|  | Fan |  | Remove all traces of dirt or scale that may upset impeller balance | 3 Months
|  | Motor |  | Clean motor | 3 Months
|  | Compressor |  | Check the air intake filter for the presence of dust | 1 Month
|  | Compressor |  | Clean all finned parts on the compressor with compressed air | 1 Year
| Filtration System | Filter elements |  | Extract filter elements from filter housing and rinse them | 1 Week
| Wet MTP - Screw Conveyor | Screw conveyor | Check oil level of gearbox; check gearbox for leakage | Remove material stuck in screw and between screw and casing | 2 Months
| Wet MTP - Mixer | Knife gate valve | Remove dirt; clean valve parts under consideration of safety instruction | Remove dirt; clean valve parts under consideration of safety instruction | 1 Month
|  | Mixer |  | Mixer cleaning from the inside | 1 Week
|  | Motor |  | Clean motor (air flow channels and ribs), fan grille and the inside of fan | 3 Months
| Wet MTP - Star Screen | Star screen |  | Remove residues and wound up material (plastic ropes and bands) if necessary | 1 Day
|  | Sprokets |  | remove dirt | 1 Week
| Wet MTP - Sand Trap & Buffer Tank | Sand trap |  | Remove wounded materials from shafts and paddles of surface scrappers | 2 Days
|  | Buffer tank |  | Remove light materials from buffer tank | 1 Week
| Wet MTP - Air Blower | Blower |  | At 450 mbar the intake filter is to be cleaned or replaced if necessary | 1 Week
|  | Motor |  | Remove oil spills and dust from the surface of housing | 3 Months
|  | Motor |  | Clean air inlet and outlet openings | 3 Months
| Wet MTP / AD - Rotacut | Rotacut |  | Remove material from Rotacut when clogged | As required
|  | RotaCut |  | Remove foreign matter from separator through cleaning port at the bottom of the pot | 3 Months
| Wet MTP / AD - Hidrostal Centrifugal Pump | Motor |  | Remove oil spills and dust accumulation from the surface of frame | 2 Weeks
|  | Motor |  | Clean inlet and outlet openings of cooling fan | 3 Months
| Sensors / Meters | Flowmeter |  | Check the metering tube for deposits and dirt and clean tube | 1 Week
| Wet MTP - Gantry Crane | Chain hoist |  | Clean chain | 1 Month
|  | Travelling machinery |  | Clean the motors | 6 Months
| AD - Hydrolyser & Digester Agitators | Gearbox |  | Clean the gear unit housing surface and fan | 1 Year
|  | Motor |  | cleanling of terminal locations and terminals | 1 Year
|  | Motor |  | Clean air-flow channels and the water chambers | 1 Year
| AD - Aeration Agitators | Gearbox |  | Clean gearbox and ventilation | 6 Months
| AD - Aerzen Blower | Axial Blower |  | clean impeller | 2 Years
|  | Axial Blower |  | Remove dirt from motor cooling fins | 2 Years
| AD - Aeration Cooling System | Chiller |  | Check that the cooling fins of the external coil are clean (if any) | 1 Month
|  | Chiller |  | Clean the exterior of the unit with water and soap (Do not use aggressive detergents) | 1 Year
| AD - Flocculation | Liquid polymer unit |  | Clean out the hopper and the wetting device where liquid polymer meets the water | 1 Month
|  | Liquid polymer unit |  | Clean screw auger and screw auger drive | 1 Month
|  | Liquid polymer unit |  | Clean the level sensor pipe | 1 Month
|  | Liquid polymer unit |  | Clean the water valves and the fast-moving machine parts on water line | 1 Week
|  | Liquid polymer unit |  | Clean the ribs and passages of motors housings | 1 Week
|  | Motor |  | Clean the housing, air-flow channels and guard of fan | 1 Year
|  | Motor |  | Change bearings, lubricant and rotary shaft seals | 5 Years
| AD - Dewatering | Decanter |  | Remove deposits from outlet orifice of feed pipe | 3 Months
|  | Decanter |  | Remove metal abrasion settled partickes at the magnetic locking screw of gear | 3 Months
|  | Bowl drive motor |  | Cleanling of terminal locations and terminals | 6 Months
|  | Bowl drive motor |  | Clean the air-flow channels and the water chamber | 1 Year
|  | Scroll drive motor |  | Clean the cooling air passages through which the ambient air flows (using dry compressed air) | 3 Months
|  | Static screen |  | Clean the screen with high pressure water jet, use brush ang detergent solution if necessary | 1 Month
| AD - Gas Bubble | Membranes |  | Soiled membranes can be cleaned either with commercially available tarpaulin cleaners or soap suds | 2 Years
| AD - Gas Booster Station | Blower |  | Clean the whole unit | 1 Week
|  | Motor |  | Clean the cooling passages through which cooling air flows | 3 Months
| AD - Flaring Unit | Flame arrester |  | Check insert for dirt. If necessary, clean with steam jet and afterwards dry and blow with compressed-air, replace seals | 1 Year
| AD - CHP | Heat exchanger |  | Clean heat exchanger. | 3 Months
|  | Water chiller |  | Cleanlining of the air-side heat exchanger | 1 Year
| Dry MTP / AD - Compressor | Compressor |  | clean the air filter | 3 Months
|  | Compressor |  | clean non-return valve | 3 Months
| AD - Burner (Boiler) | Filters |  | clean filter boxes on line, in the pump and at the nozzle | 1 Year
|  | Fan |  | Clean dust which may have accumulated inside the fan or on its blades | 1 Year
|  | Photocell |  | Clean the glass cover of photocell from any dust | 1 Year
|  | Fuel tank |  | Suck any water or other impurities present on the bottom of the tank | 5 Years
|  | Boiler |  | Clean the boiler as indicated in accompanying instruction | 1 Year