## CD78_Rev00
Weekly SAWTP Maintenance Schedule
Section | Machine/Area | Responsibility of | Maintenance | Frequency | Week 1 | Week 2 | Week 3 | Week 4 | Week 5 | Week 6 | Week 7 | Week 8 | Week 9 | Week 10 | Week 11 | Week 12 | Week 13 | Week 14 | Week 15 | Week 16 | Week 17 | Week 18 | Week 19 | Week 20 | Week 21 | Week 22 | Week 23 | Week 24 | Week 25 | Week 26 | Week 27 | Week 28 | Week 29 | Week 30 | Week 31 | Week 32 | Week 33 | Week 34 | Week 35 | Week 36 | Week 37 | Week 38 | Week 39 | Week 40 | Week 41 | Week 42 | Week 43 | Week 44 | Week 45 | Week 46 | Week 47 | Week 48 | Week 49 | Week 50 | Week 51 | Week 52
RA | Fast Roller Shutter | MTP Plant Engineer | Clean the structure, photocells, radar and hatches with damp cloth without using any solvent | 6 Months
| Outer Main Doors | MTP Plant Engineer | Clean the structure and door hinges | 6 Months
|  | Maintenance Engineer | Lubricate hinges | 6 Months
| Floor | MTP Plant Engineer | Cleaning of floor using water powerwash | Weekly
| Push Walls and Wall panels | MTP Plant Engineer | Cleaning of walls using water powerwash | 6 Months
| Air Curtains | MTP Plant Engineer | Clean the case of air curtain using a cloth with soapy water | 2 months
| Roof Lighting | Maintenance Engineer | Check and replace if necessary lighting | Monthly
| Fire Hose reel | Health and Safety Officer | Check condition and function test fire hose reel | Weekly
DRY MTP | General MTP | MTP Plant Engineer | Daily Plant cleaning after end of operation | Daily
|  |  | Thorough cleaning of equipment and flooring | Weekly
| Bag Opener | MTP Plant Engineer | Check and clean outer and inner drum side; remove wound up materials | Daily
|  |  | Remove dirt and material from beneath moving floor | Weekly
|  | Maintenance Engineer | Check clamping arms, drum & moving floor for functioning and wear | Weekly
|  |  | Clean Interior of switch box | Monthly
|  |  | Clean Oil filter | Weekly
|  |  | Clean ventilation filter (bleeder filter) | Monthly
|  |  | Lubricate bearings of drum & moving floor | 2 Weeks
|  |  | Check hydraulic oil level, re-fill if necessary | Weekly
|  |  | Checking and if necessary exchanging all wearing & electrical parts | Yearly
| Belt Conveyors (inc. ferrous & non-ferrous separators) | MTP Plant Engineer | Remove material adhered to the supports of belt in order to avoid locking of the rollers | Daily
|  |  | Clean the conveyor, remove deposits such as dust or conveyed material, particularly from walkways and guard rollers | Daily
|  | Maintenance Engineer | Greasing of roller and drum bearings | Weekly
|  |  | Check gearbox oil level, re-fill if necessary | 2 Months
|  |  | Check conveyor functionality | Weekly
| Trommel Rotary Screen | MTP Plant Engineer | Cleaning of inside drum & discharging hopper under the screen | Weekly
|  | Maintenance Engineer | Greasing of wheel support bearings | 2 Months
|  |  | Check oil level of gearboxes and re-fill if necessary | 2 Months
|  |  | Check and if necessary exchanging all wearing & electrical parts | 2 Months
| Press Compactors | MTP Plant Engineer | Clean out any waste material that has generated behind the ram and also wihtin the compactor body | Weekly
|  |  | Clean compactor rails from deposited material | Weekly
|  |  | Check for functionality before startup | Daily
|  | Maintenance Engineer | Lubricate compactor rails | Monthly
|  |  | Check oil level of hydraulic reservoir and top up if necessary | Weekly
|  |  | Check and if necessary exchange all hose joints | 6 Months
| Blower/ Baghouse filter | MTP Plant Engineer | Clean and remove material deposited on blower | Daily
|  | Maintenance Engineer | Greasing of blower bearings | Weekly
|  |  | Check oil level of air compressor and re-fill if necessary; Clean breeder filter | Weekly
|  |  | Air compressor full Service | Yearly
| Air Curtains | MTP Plant Engineer | Clean the case of air curtain using a cloth with soapy water | 2 Months
| Electrical Cabinets | Maintenance Engineer | Visual Check and inspection of electrical parts and wiring; Exchange electrical parts if necesaary | Monthly
|  |  | Thermographic Inspection | Yearly
|  | MTP Plant Engineer | Cleaning inside of electrical cabinets using air compressor | 2 months
| Sewer Holes | MTP Plant Engineer | Cleaning of sewer holes using water powerwash | 2 Weeks
WET MTP | Mixers | MTP Plant Engineer | Empty tank , empty sluice to clean from inside | Daily
|  |  | Cleaning of mixers from outside | Monthly
|  | Maintenance Engineer | Inspect gland slide valve | 2 months
|  |  | Tension v-belts | 2 months
|  |  | Lubricate bearings | 2 Weeks
|  |  | Lubricate drive motor | 2 months
|  |  | Check and if necessary exchange dispersing teeth | Monthly
| Star Screen | MTP Plant Engineer | Screen stars of the screen deck are to be checked for residues and wrapped material and cleaned if necessary | Weekly
|  | Maintenance Engineer | Check drive roller chains for free movement and lubricate | 2 Weeks
|  |  | Check screen shafts for free movement and greasing of shaft bearings | 2 Weeks
| Rotacut | MTP Plant Engineer | Empty and flush rotacut | Daily
|  |  | Cleaning of rotacut from outside and related equipment | Weekly
|  | Maintenance Engineer | Check and if necessary replace blades and screen | Weekly
|  |  | Servicing of hydraulic jack | 2 Weeks
|  |  | Check gearbox oil level, re-fill if necessary | 6 Months
| Screw Conveyors | MTP Plant Engineer | Cleaning of screw conveyors | Daily
|  | Maintenance Engineer | Checking and if necessary exchanging screws | 2 months
| WET MTP Pit | MTP Plant Engineer | Clean pit from sedimental | Weekly
| Wet MTP / AD - Hidrostal Centrifugal Pump | MTP Plant Engineer | Remove oil spills and dust accumulation from the surface of frame | 2 Weeks
|  |  | Clean inlet and outlet openings of cooling fan | Monthly
|  | Maintenance Engineer | Check oil level, re-fill if necessary | Monthly
|  |  | Checking and if necessary exchanging all wearing & electrical parts | 6 Months
AD Waste Processing | Lobe pumps | MTP Plant Engineer | Clean inlet and outlet openings of cooling fan | Monthly
|  | Maintenance Engineer | Check and if necessary replace lobes | Monthly
|  |  | Check oil level, re-fill if necessary | Monthly
| Hydrolyser | MTP Plant Engineer | Visual inspection for floating material inside the tank | Weekly
|  | Maintenance Engineer | Check water level of safety valves, top up if necessary | Weekly
|  |  | Check for agitator noises and condition | Weekly
|  |  | Greasing of shaft bearing | Monthly
|  |  | Check level of water seals, top up if necessary | Weekly
| Digesters (3) | MTP Plant Engineer | Visual inspection for floating material inside the tank | Weekly
|  | Maintenance Engineer | Check water level of safety valves, top up if necessary | Weekly
|  |  | Check for agitator noises and condition | Weekly
|  |  | Greasing of shaft bearing | Monthly
|  |  | Check level of water seals, top up if necessary | Weekly
| Digester Pit | MTP Plant Engineer | Check for pump functionality | Weekly
|  |  | Check for cleanliness | Weekly
|  |  | Check for any leakages from pumps | Daily
| Ferric Chloride Station | MTP Plant Engineer | Check for any leakages | Daily
|  |  | Check that dosing pump is working and that ferric chloride is being delivered | Daily
|  | Maintenance Engineer | Check dosing pump for noises and condition | Daily
| Dewatering Screen | MTP Plant Engineer | Check cleanliness of screen and solids container | Daily
| Dewatering Reservoir | MTP Plant Engineer | Check level of dewatering pit | Daily
| Flocculation Station | MTP Plant Engineer | Check cleanliness of flocculant tank | Daily
|  |  | Check noises and condition of flocculation pumps | Daily
|  |  | Check condition and cleanliness of glass flow meters | Daily
| Process Water Tank | MTP Plant Engineer | Check for cleanliness and for any leakages | Daily
|  |  | Check functionality of agitator | Daily
| Decanters (2) | MTP Plant Engineer | Check for noises and condition | Daily
|  |  | Check for cleanliness and for any leakages | Daily
|  | Maintenance Engineer | Greasing of bearings | Weekly
| Conveyors (2) | MTP Plant Engineer | Clean the conveyor/remove deposits | Weekly
|  | Maintenance Engineer | Check for conveyor alignment | Daily
|  |  | Greasing of conveyor bearings | Weekly
| Aeration Tanks (3) | MTP Plant Engineer | Visual inspection for floating material inside the tank | Weekly
|  | Maintenance Engineer | Check for agitator noises and condition | Weekly
| Rotacut | MTP Plant Engineer | Empty and flush rotacut | Daily
|  |  | Cleaning of rotacut from outside and related equipment | Weekly
|  | Maintenance Engineer | Check and if necessary replace blades and screen | 2 months
|  |  | Servicing of hydraulic jack | 6 Months
|  |  | Check gearbox oil level, re-fill if necessary | 6 Months
| Gas Storage | MTP Plant Engineer | Check for cleanliness of area | Daily
|  | Maintenance Engineer | Check general condition | Daily
|  |  | Check water level of safety valves | Weekly
| Gas Booster Station | MTP Plant Engineer | Check that gas cooling heat exchanger temperature is below 15⁰C | Daily
|  |  | Check noises and condition | Daily
|  |  | Check gas analyser for any fault or maintenance messages | Daily
|  | Maintenance Engineer | Greasing of atex blowers | Monthly
| CHPs (2) | MTP Plant Engineer | Check Cleanliness of area | Weekly
|  |  | Check for leakages | Daily
|  |  | Check for noises and condition | Daily
|  |  | Check level of daily oil tank | Daily
|  | Maintenance Engineer | E10 Service | 4000 OH
| Table Coolers (2) | MTP Plant Engineer | Check leakages, noises and condition | Daily
| Heat Distribution System | MTP Plant Engineer | Check noises and condition | Daily
|  |  | Check cleanliness | Daily
|  | Maintenance Engineer | Check pressure and temperature, top up if necessary | Daily
MRF | Bag Opener | MRF Plant Engineer | Check and clean drum and ripping comb; remove wound up materials | Daily
| Bag Opener | Maintenance Engineer | Lubricate bearings & chains | 2 Weeks
|  |  | Clean heat exchanger | 2 Weeks
|  |  | Check hydraulic oil level, re-fill if necessary | 2 Weeks
| Conveyors (2) | MRF Plant Engineer | Check cleanliness & remove wound up material | Daily
|  |  | Check general status of condition | Daily
|  | Maintenance Engineer | Lubricate bearings & moving parts | 2 Weeks
General | MBTs | MTP Plant Engineer | Check temperature (<25⁰C) | Daily
|  |  | Cleaning of outside panels | 2 Weeks
|  | Maintenance Engineer | Cleaning inside of electrical cabinets | 6 months
|  |  | Thermographic Inspection | Yearly
| Boge Compressors | MTP Plant Engineer | Check for any onscreen faults | Daily
|  |  | Check for functionality | Daily
|  | Maintenance Engineer | Check oil level of air compressor and re-fill if necessary; Clean breeder filter | Weekly
Legend
Planned
Conducted