## Programme - Phase 1 & 2
Week | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
1 | Quaterly + Weekly | Yearly + weekly | Weekly | Quaterly + Weekly | Weekly | Weekly | Quaterly + Weekly | Weekly | Weekly | Quaterly + Weekly | Weekly | Weekly
2 | 1/2 yearly + weekly | Weekly | Weekly | Weekly | Weekly | Weekly | 1/2 yearly + weekly | Weekly | Weekly | Weekly | Weekly | Weekly
3 | Monthly check + weekly | Monthly check + weekly | Monthly check + weekly | Monthly check + weekly | Monthly check + weekly | Monthly check + weekly | Monthly check + weekly | Monthly check + weekly | Monthly check + weekly | Monthly check + weekly | Monthly check + weekly | Monthly check + weekly
4 | Weekly | Weekly | Weekly | Weekly | Weekly | Weekly | Weekly | Weekly | Weekly | Weekly | Weekly | Weekly

## Maintenance - Phase 1 & 2
Plant | Position | Component | Term | Maintenance work | Time required in minutes.
RTO 2 | 26 | Manual butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 5
RTO 2 | 31 | Pneumatic butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 15
RTO 2 | 37 | Pneumatic butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 15
RTO 2 | 38 | Pneumatic butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 15
RTO 2 | 72 | Pneumatic butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 15
RTO 2 | 73 | Pneumatic butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 15
RTO 2 | 75 | Pneumatic butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 15
RTO 2 | 90 | Ball valve | quarterly | Check funtion and smooth running. Check for any leakages. | 10
RTO 2 | 170 | Gas Filter | quarterly | Exchange filter. Check for any leakages | 30
RTO 2 | 171 | Gas Filter | quarterly | Exchange filter. Check for any leakages | 30
RTO 2 | 187 | Bellow expansion joint | quarterly | Visual inspection, check for any leakages | 5
RTO 2 | 188 | Bellow expansion joint | quarterly | Visual inspection, check for any leakages | 5
RTO 2 | 189 | Bellow expansion joint | quarterly | Visual inspection, check for any leakages | 5
RTO 2 | 220 | Radial fan | quarterly | Visual inspection, check functioning. | 15
RTO 2 | 301 | Pressure transmitter | 1/2 yearly | Visual inspection. Measure output signal and compare with effective pressure. | 15
RTO 2 | 303 | Differential pressure transmitter | quarterly | Visual inspection, functional test. | 15
RTO 2 | 304 | Differential pressure transmitter | quarterly | Visual inspection, functional test. | 15
RTO 2 | 305 | Pressure transducer with transmitter. | quarterly | Measure outlet signal and compare to actual pressure, readjust if necessary. | 15
RTO 2 | 306 | Pressure transmitter. | 1/2 yearly | Measure outlet signal and compare to actual pressure, readjust if necessary. | 15
RTO 2 | 330 | Thermometer | 1/2 yearly | Visual inspection. | 5
RTO 2 | 340 | Temperature switch | quarterly | Visual inspection, check functioning and settings. | 10
RTO 2 | 351 | Pressure Gauge (positive) | quarterly | Visual inspection, check functioning. | 5
RTO 2 | 360.6 | Flow rate measuring device | weekly | Record values-weekly, | 5
RTO 2 | 360.6 | Flow rate measuring device | quarterly | functional control-quarterly | 15
RTO 2 | 360.7 | Flow rate measuring device | weekly | Record values-weekly, | 5
RTO 2 | 360.7 | Flow rate measuring device | quarterly | functional control-quarterly | 15
RTO 2 | 380 | Platinum Thermometer | quarterly | Visual inspection, check functioning. | 10
RTO 2 | 380.1 | Platinum Thermometer | quarterly | Visual inspection, check functioning. | 10
RTO 2 | 380.3 | Platinum Thermometer | quarterly | Visual inspection, check functioning. | 10
RTO 2 | 380.4 | Platinum Thermometer | quarterly | Visual inspection, check functioning. | 10
RTO 2 | 430 | Gas Detector Type FGD10A Infrared | weekly | Check zero point and sensitivity calibration. | 15
RTO 2 | 430 | Gas Detector Type FGD10A Infrared | 1/2 yearly | Check display of transmitter and central unit match. Calibrate if necessary | 20
RTO 2 | 431 | Drager Polytron 8000 | yearly | Inspection by drager service | To be done by a professional technical person
RTO 2 | 601 | purge cleaner | 1/2 yearly | Visual inspection. | 30
RTO 2 | 804 | stack | 1/2 yearly | Visual inspection. | 15
RTO 2 | 951 | VocsiBox | weekly | Observe change over the poppet valves | 30
RTO 2 | 951 | VocsiBox | 1/2 yearly | Visual check of Vocsibox and piping: leakages, discoloration (hotspots), smoke, tightness of bolts and condition of sealings. | 15
RTO 2 | 951 | VocsiBox | yearly | Replace thermocouples, check wiring. | 120
RTO 2 | 951 | VocsiBox | yearly | Check state and quantity of ceramic material. | 120
RTO 2 | 951 | VocsiBox | yearly | Check for condensate. | 60
RTO 2 | 951 | VocsiBox | yearly | Visual check of poppet valves. | 120
RTO 2 | 951 | VocsiBox | yearly | Replace bearing, check shaft and poppet valves adjustment. | To be done by a professional technical person
RTO 2 | 952 | VocsiBox | yearly | Check resistance between phases. | To be done by a professional technical person
RTO 2 | 50001 | screws, flanges, pipe joints | 1/2 yearly | Visual inspection, tighten were necessary. | 10
PID Phase 1 & 2 | 20 | Manual butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 5
PID Phase 1 & 2 | 21 | Manual butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 5
PID Phase 1 & 2 | 22 | Manual butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 5
PID Phase 1 & 2 | 23 | Manual butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 5
PID Phase 1 & 2 | 30 | Pneumatic butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 15
PID Phase 1 & 2 | 31 | Pneumatic butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 15
PID Phase 1 & 2 | 32 | Pneumatic butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 15
PID Phase 1 & 2 | 33 | Pneumatic butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 15
PID Phase 1 & 2 | 50 | 3/2-way solenoid valve | quarterly | Check funtion and smooth running. Check for any leakages. | 10
PID Phase 1 & 2 | 51 | 2/2-way valve | quarterly | Check funtion and smooth running. Check for any leakages. | 10
PID Phase 1 & 2 | 90 | Ball valve | quarterly | Check funtion and smooth running. Check for any leakages. | 10
PID Phase 1 & 2 | 92 | Ball valve | quarterly | Check funtion and smooth running. Check for any leakages. | 10
PID Phase 1 & 2 | 150 | Swing check valve | quarterly | Check funtion and smooth running. Check for any leakages. | 15
PID Phase 1 & 2 | 151 | Swing check valve | quarterly | Check funtion and smooth running. Check for any leakages. | 15
PID Phase 1 & 2 | 160 | Flame arrestor | quarterly | Dismantle flame arrestor and clean with power wash and compressed air. Check/replace seals and check for any leakages. Check function of temperature controller. | 240
PID Phase 1 & 2 | 161 | Flame arrestor | quarterly | Dismantle flame arrestor and clean with power wash and compressed air. Check/replace seals and check for any leakages. Check function of temperature controller. | 240
PID Phase 1 & 2 | 162 | Flame arrestor | quarterly | Dismantle flame arrestor and clean with power wash and compressed air. Check/replace seals and check for any leakages. Check function of temperature controller. | 240
PID Phase 1 & 2 | 170 | Gas Filter | quarterly | Exchange filter. Check for any leakages | 15
PID Phase 1 & 2 | 180 | Bellow expansion joint | quarterly | Visual inspection, check for any leakages | 5
PID Phase 1 & 2 | 181 | Bolts DN80 | quarterly | Visual inspection, check for any leakages | 5
PID Phase 1 & 2 | 182 | Bellow expansion joint | quarterly | Visual inspection, check for any leakages | 5
PID Phase 1 & 2 | 183 | Bolts DN100 | quarterly | Visual inspection, check for any leakages | 5
PID Phase 1 & 2 | 184 | Bellow expansion joint | quarterly | Visual inspection, check for any leakages | 5
PID Phase 1 & 2 | 220 | Booster | quarterly | Visual inspection. Grease if necessary and chech drivebelts | 30
PID Phase 1 & 2 | 221 | Booster | quarterly | Visual inspection. Grease if necessary and chech drivebelts | 30
PID Phase 1 & 2 | 300 | Pressure transducer | 1/2 yearly | Visual inspection. Measure output signal and compare with effective pressure. | 15
PID Phase 1 & 2 | 330 | Thermometer | 1/2 yearly | Visual inspection. | 5
PID Phase 1 & 2 | 340 | Temperature switch | quarterly | Visual inspection, check functioning and settings. | 10
PID Phase 1 & 2 | 350 | Pressure Gauge (negative) | 1/2 yearly | Visual inspection, check functioning. | 5
PID Phase 1 & 2 | 351 | Pressure Gauge (positive) | quarterly | Visual inspection, check functioning. | 5
PID Phase 1 & 2 | 360 | Flow rate measuring device | weekly | Record values-weekly, | 5
PID Phase 1 & 2 | 360 | Flow rate measuring device | quarterly | functional control-quarterly | 10
PID Phase 1 & 2 | 361 | Flow rate measuring device | weekly | Record values-weekly, | 5
PID Phase 1 & 2 | 361 | Flow rate measuring device | quarterly | functional control-quarterly | 10
PID Phase 1 & 2 | 380 | Platinum Thermometer | quarterly | Visual inspection, check functioning. | 10
PID Phase 1 & 2 | 430 | Control cabinet's solenoid valves, | quarterly | Visual inspection and check functioning | 10
PID Phase 1 & 2 | 430 | Control cabinet's heating tape and terminal cables | monthly | Check function. | 10
PID Phase 1 & 2 | 430 | Control cabinet's flame arrestor | quarterly | Visual inspection, check functioning and clean if necessary. | 10
PID Phase 1 & 2 | 430 | Control cabinet's pressure controllers | quarterly | Check function and settings | 10
PID Phase 1 & 2 | 430 | Control cabinet's electric gas cooler | quarterly | Must be maintained clean. | 10
PID Phase 1 & 2 | 430 | Control cabinet's alarm sensors | quarterly | Visual inspection, check functioning and clean if necessary. | 10
PID Phase 1 & 2 | 430 | Control cabinet's gasoline filter | quarterly | Exchange filter. Check for any leakages | 10
PID Phase 1 & 2 | 430 | Control cabinet's hose pump | quarterly | Exchange hose. Check for any leakages | 10
PID Phase 1 & 2 | 430 | Control cabinet's filter. | quarterly | Visual inspection, check functioning and clean if necessary. | 10
PID Phase 1 & 2 | 430 | Siemens ULTRAMAT+C51 gas analyzer | quarterly | Check function. | 10
PID Phase 1 & 2 | 500 | control cabinet with burner control BCU460 | quarterly | Check safety function. | 10
PID Phase 1 & 2 | 520 | Flashlight red | quarterly | Check function. | 5
PID Phase 1 & 2 | 530 | Signalling Horn | quarterly | Check function. | 5
PID Phase 1 & 2 | 541 | Load break switch | quarterly | Check function. | 5
PID Phase 1 & 2 | 680 | Boge screw compressor suction filter | monthly | Visual inspection. Clean or change. | 15
PID Phase 1 & 2 | 680 | Boge screw compressor's oil change | yearly | Oil change | 30
PID Phase 1 & 2 | 680 | Boge screw compressor's check safety valve | yearly | Check function. | 15
PID Phase 1 & 2 | 680 | Boge screw compressor's check oil level | 1/2 yearly | Check oil level, top up if necessary. | 30
PID Phase 1 & 2 | 680 | Boge screw compressor's change oil filter & separator- | yearly | Change oil separator and filter. | 30
PID Phase 1 & 2 | 780 | Container | quarterly | Visual inspection. Any paint defects should be noted and repaired instantly. | 10
PID Phase 1 & 2 | 930 | condenate separator | quarterly | Visual inspection, check functioning, clean if necessary. | 20
PID Phase 1 & 2 | 931 | condenate separator | quarterly | Visual inspection, check functioning, clean if necessary. | 20
PID Phase 1 & 2 | 50001 | screws, flanges, pipe joints | 1/2 yearly | Visual inspection, tighten were necessary. | 10
Booster Station | 20 | Manual butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 5
Booster Station | 21 | Manual butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 5
Booster Station | 30 | Pneumatic butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 15
Booster Station | 31 | Pneumatic butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 15
Booster Station | 90 | Ball valve | quarterly | Check funtion and smooth running. Check for any leakages. | 10
Booster Station | 92 | Ball valve | quarterly | Check funtion and smooth running. Check for any leakages. | 10
Booster Station | 150 | Swing check valve | quarterly | Check funtion and smooth running. Check for any leakages. | 15
Booster Station | 151 | Swing check valve | quarterly | Check funtion and smooth running. Check for any leakages. | 15
Booster Station | 160 | Flame arrestor | quarterly | Dismantle flame arrestor and clean with power wash and compressed air. Check/replace seals and check for any leakages. Check function of temperature controller. | 240
Booster Station | 161 | Flame arrestor | quarterly | Dismantle flame arrestor and clean with power wash and compressed air. Check/replace seals and check for any leakages. Check function of temperature controller. | 240
Booster Station | 180 | Bellow expansion joint | quarterly | Visual inspection, check for any leakages | 5
Booster Station | 184 | Bellow expansion joint | quarterly | Visual inspection, check for any leakages | 5
Booster Station | 220 | Booster | quarterly | Visual inspection. Grease if necessary and chech drivebelts | 30
Booster Station | 221 | Booster | quarterly | Visual inspection. Grease if necessary and chech drivebelts | 30
Booster Station | 300 | Pressure transducer | 1/2 yearly | Visual inspection. Measure output signal and compare with effective pressure. | 15
Booster Station | 330 | Thermometer | 1/2 yearly | Visual inspection. | 5
Booster Station | 340 | Temperature switch | quarterly | Visual inspection, check functioning and settings. | 10
Booster Station | 350 | Pressure Gauge (negative) | 1/2 yearly | Visual inspection, check functioning. | 5
Booster Station | 351 | Pressure Gauge (positive) | quarterly | Visual inspection, check functioning. | 5
Booster Station | 360 | Flow rate measuring device | weekly | Record values-weekly, | 5
Booster Station | 360 | Flow rate measuring device | quarterly | functional control-quarterly | 10
Booster Station | 360.2 | Flow rate measuring device | weekly | Record values-weekly, | 5
Booster Station | 360.2 | Flow rate measuring device | quarterly | functional control-quarterly | 10
Booster Station | 380 | Platinum Thermometer | quarterly | Visual inspection, check functioning. | 10
Booster Station | 930 | condensate separator | quarterly | Visual inspection, check functioning, clean if necessary. | 20
Booster Station | 931 | condensate separator | quarterly | Visual inspection, check functioning, clean if necessary. | 20
Booster Station | 50001 | screws, flanges, pipe joints | 1/2 yearly | Visual inspection, tighten were necessary. | 10
RTO 1 | 20 | Manual butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 5
RTO 1 | 21 | Manual butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 5
RTO 1 | 30 | Pneumatic butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 15
RTO 1 | 31 | Pneumatic butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 15
RTO 1 | 90 | Ball valve | quarterly | Check funtion and smooth running. Check for any leakages. | 10
RTO 1 | 92 | Ball valve | quarterly | Check funtion and smooth running. Check for any leakages. | 10
RTO 1 | 150 | Swing check valve | quarterly | Check funtion and smooth running. Check for any leakages. | 15
RTO 1 | 151 | Swing check valve | quarterly | Check funtion and smooth running. Check for any leakages. | 15
RTO 1 | 160 | Flame arrestor | quarterly | Dismantle flame arrestor and clean with power wash and compressed air. Check/replace seals and check for any leakages. Check function of temperature controller. | 240
RTO 1 | 161 | Flame arrestor | quarterly | Dismantle flame arrestor and clean with power wash and compressed air. Check/replace seals and check for any leakages. Check function of temperature controller. | 240
RTO 1 | 180 | Bellow expansion joint | quarterly | Visual inspection, check for any leakages | 5
RTO 1 | 184 | Bellow expansion joint | quarterly | Visual inspection, check for any leakages | 5
RTO 1 | 220 | Booster | quarterly | Visual inspection. Grease if necessary and chech drivebelts | 30
RTO 1 | 221 | Booster | quarterly | Visual inspection. Grease if necessary and chech drivebelts | 30
RTO 1 | 300 | Pressure transducer | 1/2 yearly | Visual inspection. Measure output signal and compare with effective pressure. | 15
RTO 1 | 330 | Thermometer | 1/2 yearly | Visual inspection. | 5
RTO 1 | 340 | Temperature switch | quarterly | Visual inspection, check functioning and settings. | 10
RTO 1 | 350 | Pressure Gauge (negative) | 1/2 yearly | Visual inspection, check functioning. | 5
RTO 1 | 351 | Pressure Gauge (positive) | quarterly | Visual inspection, check functioning. | 5
RTO 1 | 360 | Flow rate measuring device | weekly | Record values-weekly, | 5
RTO 1 | 360 | Flow rate measuring device | quarterly | functional control-quarterly | 10
RTO 1 | 360.2 | Flow rate measuring device | weekly | Record values-weekly, | 5
RTO 1 | 360.2 | Flow rate measuring device | quarterly | functional control-quarterly | 10
RTO 1 | 380 | Platinum Thermometer | quarterly | Visual inspection, check functioning. | 10
RTO 1 | 930 | condensate separator | quarterly | Visual inspection, check functioning, clean if necessary. | 20
RTO 1 | 931 | condensate separator | quarterly | Visual inspection, check functioning, clean if necessary. | 20
RTO 1 | 50001 | screws, flanges, pipe joints | 1/2 yearly | Visual inspection, tighten were necessary. | 10
Flare 1 | 20 | Manual butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 15
Flare 1 | 24 | Manual butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 15
Flare 1 | 30 | Pneumatic butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 15
Flare 1 | 35 | Pneumatic butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 15
Flare 1 | 52 | 2/2-way valve | quarterly | Check funtion and smooth running. Check for any leakages. | 15
Flare 1 | 90 | Ball valve | quarterly | Check funtion and smooth running. Check for any leakages. | 15
Flare 1 | 93 | Ball valve | quarterly | Check funtion and smooth running. Check for any leakages. | 10
Flare 1 | 160 | Flame arrestor | quarterly | Dismantle flame arrestor and clean with power wash. | 240
Flare 1 | 165 | Flame arrestor | yearly | Dismantle flame arrestor and clean. | 240
Flare 1 | 166 | Flame arrestor | quarterly | Dismantle flame arrestor and clean with power wash. | 240
Flare 1 | 184 | Bellow expansion joint | quarterly | Visual inspection, check for any leakages | 5
Flare 1 | 290 | Tank regulator | Everytime cylinder change. | Check for leakages. | 5
Flare 1 | 301 | Pressure transducer | 1/2 yearly | Visual inspection. Measure output signal and compare with effective pressure. | 15
Flare 1 | 310 | Pressure switch | quarterly | check funcion. | 15
Flare 1 | 330 | Thermometer | 1/2 yearly | Visual inspection. | 5
Flare 1 | 340 | Temperature switch | quarterly | Visual inspection, check functioning and settings. | 15
Flare 1 | 351 | Pressure Gauge (positive) | quarterly | Visual inspection, check functioning. | 5
Flare 1 | 360.3 | Flow rate measuring device | weekly | Record values-weekly, | 15
Flare 1 | 360.3 | Flow rate measuring device | quarterly | functional control-quarterly | 30
Flare 1 | 501 | Terminal box | 1/2 yearly | Visual Inspection | 15
Flare 1 | 630 | Gas cylinder | quarterly | Check for leakages. Check valve by open and closing. | 15
Flare 1 | 801 | Flare | quarterly | Burner; check for scale loss and flame aspect, readjust, if necessary check admisson pressure of the flare as well as the flow pressure and the flow rate and note them down | 60
Flare 1 | 801 | Flare | quarterly | combustion chamber; check for scale loss and wear and tear. | 30
Flare 1 | 801 | Flare | quarterly | check flare isolation. | 30
Flare 1 | 820 | louver for flare | quarterly | visual control, check funtionand clean if necessarry | 30
Flare 1 | 830 | louver motor | quarterly | Visual inspection, check functioning. | 30
Flare 1 | 850 | UV sensor | quarterly | Visual inspection, check functioning. Change every 10,000 hours. | 30
Flare 1 | 860 | Ignition electrode | quarterly | Check ignition, ceramics and ignition distance | 30
Flare 1 | 861 | Plug for ignition electrode | quarterly | Visual inspection. | 30
Flare 1 | 910 | Ignition transformer | quarterly | Visual inspection, check functioning. | 30
Flare 1 | 920 | Thermocouple | quarterly | Visual inspection, check functioning. | 30
Flare 1 | 921 | Connection for thermocouple | quarterly | Visual inspection, check functioning. | 30
Flare 1 | 50001 | screws, flanges, pipe joints | 1/2 yearly | Visual inspection, tighten were necessary. | 60
Flare 2 | 22 | Manual butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 5
Flare 2 | 34 | Pneumatic butterfly valve | quarterly | Check funtion and smooth running. Check for any leakages. | 15
Flare 2 | 52 | 2/2-way valve | quarterly | Check funtion and smooth running. Check for any leakages. | 10
Flare 2 | 90 | Ball valve | quarterly | Check funtion and smooth running. Check for any leakages. | 10
Flare 2 | 93 | Ball valve | quarterly | Check funtion and smooth running. Check for any leakages. | 10
Flare 2 | 162 | Flame arrestor | quarterly | Dismantle flame arrestor and clean with power wash and compressed air. Check/replace seals and check for any leakages. Check function of temperature controller. | 240
Flare 2 | 165 | Flame arrestor | yearly | Visual inspection, clean if necessary | 240
Flare 2 | 180 | Bellow expansion joint | quarterly | Visual inspection, check for any leakages | 5
Flare 2 | 290 | Tank regulator | Everytime cylinder change. | Check for leakages. | 5
Flare 2 | 301 | Pressure transducer | 1/2 yearly | Visual inspection. Measure output signal and compare with effective pressure. | 15
Flare 2 | 310 | Pressure switch | quarterly | check funcion. | 10
Flare 2 | 330 | Thermometer | 1/2 yearly | Visual inspection. | 5
Flare 2 | 340 | Temperature switch | quarterly | Visual inspection, check functioning and settings. | 10
Flare 2 | 351 | Pressure Gauge (positive) | quarterly | Visual inspection, check functioning. | 5
Flare 2 | 360.2 | Flow rate measuring device | weekly | Record values-weekly, | 5
Flare 2 | 360.2 | Flow rate measuring device | quarterly | functional control-quarterly | 20
Flare 2 | 501 | Terminal box | 1/2 yearly | Visual Inspection | 5
Flare 2 | 630 | Gas cylinder | quarterly | Check for leakages. Check valve by open and closing. | 5
Flare 2 | 800 | Flare | quarterly | Burner; check for scale loss and flame aspect, readjust, if necessary check admisson pressure of the flare as well as the flow pressure and the flow rate and note them down | 60
Flare 2 | 800 | Flare | quarterly | combustion chamber; check for scale loss and wear and tear. | 15
Flare 2 | 800 | Flare | quarterly | check flare isolation. | 15
Flare 2 | 820 | louver for flare | quarterly | visual control, check funtionand clean if necessarry | 20
Flare 2 | 830 | louver motor | quarterly | Visual inspection, check functioning. | 15
Flare 2 | 850 | UV sensor | quarterly | Visual inspection, check functioning. Change every 10,000 hours. | 20
Flare 2 | 860 | Ignition electrode | quarterly | Check ignition, ceramics and ignition distance | 20
Flare 2 | 861 | Plug for ignition electrode | quarterly | Visual inspection. | 5
Flare 2 | 910 | Ignition transformer | quarterly | Visual inspection, check functioning. | 5
Flare 2 | 920 | Thermocouple | quarterly | Visual inspection, check functioning. | 5
Flare 2 | 921 | Connection for thermocouple | quarterly | Visual inspection, check functioning. | 5
Flare 2 | 50001 | screws, flanges, pipe joints | 1/2 yearly | Visual inspection, tighten were necessary. | 10

## Maintenance - CHP
CHP Maintenance Schedule
Interval/Running Hours
Operation | Code | 20-50 | 500-1000 | 2000 | 4000 | 8000 | 14000 | 28000 | 56000
Leak Test | W-1001 | X | X
Check Screw Connections | W-1002 | X | X
Engine Oil/Analysis | W-1003 | X | X
Change Oil Filter | W-1004 | X | X
Check Start Function | W-1005 | X | X
Ignition Plug Check/Change | W-1007 |  | X
Notice Operating Data | W-1006 | X
Check Valve Clearance | W-1009 | X |  | X
Check Jacked Water Circuit | W-1011 | X |  | X
Change Air Filter | W-1008 |  |  | X
Clean speed sensor | W-1016 |  |  |  | X
Check time of Ignition | W-1010 | X |  |  | X
Check crankcase pressure | W-1012 | X |  |  | X
Check exhaust back pressure | W-1012 | X |  |  | X
Check exhaust emissions | W-1014 | X |  |  | X
Check control panel | W-1018 | X |  |  | X
Check/Clean mixture cooler | W-1017 |  |  |  | X
Check gas mixture | W-1020 |  |  |  | X
Check trottle valve | W-1025 |  |  |  | X
Check ignition system | W-1026 |  |  |  | X
Change gas filter | W-1022 | X |  |  | X
Check engine bearing | W-1027 |  |  |  |  | X
Check ignition cable | W-1028 |  |  |  |  | X
Check terminal generator cable | W-1021 | X |  |  |  | X
Change coolant | W-1023 | [5 empty] | X
Change turbo charger | W-1024 | [5 empty] | X
Change oil separator | W-1029 | [5 empty] | X
Change deflagration protector | W-1035 | [5 empty] | X
Change liners | W-1031 | [6 empty] | X
Change connecting-rod bearing | W-1032 | [6 empty] | X
Change piston rings | W-1033 | [6 empty] | X
Change cylinder head | W-1034 | [6 empty] | X
Change piston | W-1036 | [7 empty] | X
Change crankshaft bearing | W-1037 | [7 empty] | X
Change valve control | W-1038 | [7 empty] | X
Check/Change connecting-rod | W-1039 | [7 empty] | X
Check camshaft | W-1040 | [7 empty] | X
Check crankshaft | W-1041 | [7 empty] | X
Change elastic coupling | W-1042 | [7 empty] | X